## Report Sheet
STORE #: | [23 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | [23 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | SELECT FROM DROP DOWN LIST | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | [24 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | [24 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | YHC072E3RMA0M3Q | 103912538L | RTU-1 | KITCHEN | 500 | 632 | 0 | 0 |  | 1674 |  | 932 |  | 1 | 209.6 | 209.6 | 3 | 4 | 4.26 | 4.13 | 1.4926 | 1.447 | -3.052%
YORK | YHC092E3RHA0M3Q | 104010715L | RTU-2 | DINING | 1000 | 712 | 600 | 712 |  | 1126 | 1126 | 1126 | 1126 | NL | 209.3 | 209.3 | 3 | 8.5 | 6.46 | 6.46 | 2.2602 | 2.2602 | 0%
CAPTIVE AIRE | D76 | 1217059 | MUA-1 | HOOD 1 | 1425 | 1235 | 1000 | 1235 | No | 2152 | 2152 | 1758 | 2152 | 1.5 | 208.9 | 208.9 | 3 | 4.7 | 3.6 | 3.6 | 1.2571 | 1.2571 | 0%
CAPTIVE AIRE | DU85HFA | 2853405 | EF-1 | HOOD 1 | 2150 | 3183 | 1700 | 1747 | No | 1215 | 1143 | 1215 | 1143 | 0.75 | 119.4 | 118.5 | 1 | 7.2 | 8 | 6.1 | 1.5967 | 1.2083 | -24.32%
| RR FAN RUNNING? | No | EF-2 | RESTROOM | 150 | 0 | 150 | 0
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 2925 | 2579 | 1600 | 1947 |  | FRONT DOOR |  | 0.0051 |  |  | INITIAL | 6.6067 | 2579
|  |  | TOTAL EXHAUST |  | 2300 | 3183 | 1850 | 1747 |  | BACK DOOR |  | 0.0047 |  |  | FINAL | 6.1727 | 1947
|  |  | NET AIRFLOW |  | 625 | -604 | -250 | 200 |  | AVERAGE |  | 0.0049 |  |  | ∆ | -0.43395 | -632
Issue List
Unit # | Description
Select from drop down list
Additional Notes: | Unable to adjust pulley setpoints on MUA to increase speed.

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
EF / Not operational / The EF is not operational. Recommend servicing.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not operational / MUA is not operational. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / OA Filters / OA filters are not installed. Recommend installing
RTU / Thermostats / Gridpoint stats are in Fan Auto. Recommend programming for Fan on except if kitchen RTU is balanced for 0 CFM OA.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.