## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4110 | 4129 | 3310 | 3364 | 800 | 765 | 19.46% | 18.53%
RTU-2 | KITCHEN | 3000 | 2973 | 2600 | 2537 | 400 | 436 | 13.33% | 14.67%
MUA-1 | MUA | [8 empty] | 2821 | 2838
EF-1 | FRYERS | [10 empty] | 1662 | 1584
EF-2 | GRILL | [10 empty] | 1852 | 1882
EF-3 | TOILET/MOP SINK | [12 empty] | 225 | 222
TOTALS |  | 7110 | 7102 | 5910 | 5901 | 1200 | 1201 |  |  | 2821 | 2838 | 3514 | 3466 | 225 | 222
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4021 | 4039 |  | FRONT |  | 0.02 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 3739 | 3688 |  | SIDE |  | -0.01 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 282 | 351 |  | REAR |  | -0.02 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0033333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Wind along side of building affecting pressure measurements.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0