## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3350 | 3465 | 2780 | 2913 | 570 | 552 | 17.01% | 15.93%
RTU-2 | KITCHEN | 3275 | 2983 | 2620 | 2309 | 655 | 674 | 20% | 22.59%
MUA-1 | COOKLINE | [8 empty] | 1976 | 1905
KEF-1 | KITCHEN HD | [10 empty] | 2381 | 2396
CEF-1 | WOMENS RR | [12 empty] | 100 | 113
CEF-2 | MENS RR | [12 empty] | 100 | 101
TOTALS |  | 6625 | 6448 | 5400 | 5222 | 1225 | 1226 |  |  | 1976 | 1905 | 2381 | 2396 | 200 | 214
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3201 | 3131 |  | FRONT |  | 0.0059 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2581 | 2610 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 620 | 521 |  | REAR |  | 0.0017 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0038 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0