## Report Sheet
STORE #: | [23 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | NEW PHILADELPHIA, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-03-23 |  | ` | [21 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST / MOHAMMED OUARD | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZJ078N18D2B5EAA2A1 | N1C7534763 | RTU-1 | KITCHEN | 500 | 410 | 0 | 0 |  | 1762 | 1762 | 925.3 | 925.3 | 2 | 213.5 | 213.5 | 3 | 6.3 | 4.38 | 4.38 | 1.5632 | 1.5632 | 0%
YORK | ZJ090N18D2B5EAA2A1 | N1C7528142 | RTU-2 | DINING | 1000 | 164 | 1000 | 164 |  | 1751 | 1751 | 930 | 930 | 3 | 213.6 | 213.6 | 3 | 9.5 | 6.08 | 6.08 | 2.1709 | 2.1709 | 0%
CAPTIVE AIRE | A1-D.250-G10 | 2932641 | MUA-1 | HOOD 1 | 1950 | 1574 | 1700 | 1760 | No | 1775 | 1769 | 1068 | 1179 | 2 | 213.3 | 213.6 | 3 | 5.95 | 2.58 | 2.99 | 0.91992 | 1.0676 | 16.05%
CAPTIVE AIRE | NCA24HPFA | 2932641 | EF-1 | HOOD 1 | 3200 | 2157 | 2450 | 2464 | No | 1756 | 1747 | 875 | 915 | 2 | 213.1 | 212.9 | 3 | 5.95 | 3.81 | 4.17 | 1.3572 | 1.4841 | 9.346%
| RR FAN RUNNING? | Choose Yes or No: | EF-2 | RESTROOM | 150 | 0 | 150 | 0
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 2148 | 2700 | 1924 |  | FRONT DOOR |  | 0.11 |  |  | INITIAL | 6.0113 | 2148
|  |  | TOTAL EXHAUST |  | 3350 | 2157 | 2600 | 2464 |  | BACK DOOR |  | 0.09 |  |  | FINAL | 6.2858 | 1924
|  |  | NET AIRFLOW |  | 100 | -9 | 100 | -540 |  | AVERAGE |  | 0.1 |  |  | ∆ | 0.27454 | -224
Issue List
Unit # | Description
Select from drop down list
EF-RR | NOT OPERATIONAL UPON ARRIVAL,
RTU-1 | NO CONTROLS FOR ECON ON BOARD, OA DAMPER CLOSED MANUALLY
RTU-2 | RTU / OA Damper / Outside air damper is not functional and OA could not be set.
Additional Notes:

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
EF / Not operational / The EF is not operational. Recommend servicing.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not operational / MUA is not operational. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / OA Filters / OA filters are not installed. Recommend installing
RTU / Thermostats / Gridpoint stats are in Fan Auto. Recommend programming for Fan on except if kitchen RTU is balanced for 0 CFM OA.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.