## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | FRONT ENTRANCE | 4000 | 4284 | 3600 | 3887 | 400 | 397 | 10% | 9.267%
AC-2 | STOCK ROOM | 4300 | 4366 | 3870 | 4366 | 430 | 0 | 10% | 0%
AC-3 | PHARMACY | 1000 | 1070 | 900 | 965 | 100 | 105 | 10% | 9.813%
AHU-4 | MAIN STORE | 35000 | 32308 | 35000 | 32308 | 0 | 0 | 0% | 0%
DOAS-1 | MAIN STORE | [8 empty] | 6000 | 6086
SF-1 | DELI HOOD | [8 empty] | 1920 | 1953
EF-1 | DELI HOOD | [10 empty] | 2400 | 2590
EF-2 | RACK OVEN | [10 empty] | 800 | 874
EF-3 | RESTROOMS | [12 empty] | 200 | 194
EF-4 | PHARMACY RESTROOM | [12 empty] | 90 | 94
EF-5 | BREAK ROOM | [12 empty] | 600 | 654
EF-6 | RESTROOM | [12 empty] | 750 | 696
EF-7 | MESSANINE RESTROOM | [12 empty] | 500 | 472
EF-8 | MEAT/SEAFOOD | [12 empty] | 1650 | 1524
EF-9 | ELECTRIACL ROOM | [12 empty] | 400 | 0
EF-10 | MECH ROOM | [12 empty] | 1600 | 721
EF-11 | MECH ROOM | [12 empty] | 1420 | 631
TOTALS |  | 44300 | 42028 | 43370 | 41526 | 930 | 502 |  |  | 7920 | 8039 | 3200 | 3464 | 7210 | 4986
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | TRUE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 8850 | 8541 |  | FRONT | [10 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 10410 | 8450 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | -1560 | 91 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
OPEN GROCERY STORE WITH AUTOMATIC SLIDING DOORS. UNABLE TO TEST BUILDING PRESSURE.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0