## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5250 | 5366 | 3750 | 3585 | 1500 | 1781 | 28.57% | 33.19%
RTU-2 | BOH | 2100 | 1715 | 1600 | 1403 | 500 | 312 | 23.81% | 18.19%
RTU-3 | KITCHEN | 4200 | 4215 | 2665 | 2307 | 1535 | 1908 | 36.55% | 45.27%
KEF-1 | GRILL HOOD | [10 empty] | 1994 | 0
KEF-2 | FRYER HOOD | [10 empty] | 1091 | 0
EF-1 | RESTROOMS | [12 empty] | 300 | 0
TOTALS |  | 11550 | 11296 | 8015 | 7295 | 3535 | 4001 |  |  | 0 | 0 | 3085 | 0 | 300 | 0
[16 empty] | TRUE | FALSE | FALSE
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1 | TRUE | FALSE | FALSE
TOTAL OA |  | 3535 | 4001 |  | FRONT |  | 0.0308
TOTAL EXHAUST |  | 3385 | 0 |  | SIDE |  | 0.0312 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1 | FALSE
NET AIRFLOW |  | 150 | 4001 |  | REAR |  | 0.0306
[5 empty] | AVERAGE |  | 0.030867
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0