## Sheet1
APPENDIX *RTU (ROOFTOP UNIT) *EH (ENTRY HEATER) *ERV (ENERGY RECOVERY VENTILATOR) *EF (EXHAUST FAN) *CU (SPLIT SYSTEM- COMPRESOR UNIT) *AHU(SPLIT SYSTEM-AIR HANDLER) |  |  | WALGREENS FY24 HVAC SITE SURVEY CHECKLIST
Date: | 2025-05-01 | Store#: | 13000 | Address: | 860 EAST AVE, CHICO, CA 95926
| EQUIPMENT DATA | [7 empty] | COOLING | HEATING |  | SMOKE DETECTOR |  | POWER SUPPLY |  |  |  | RTU/ROOF |  |  | CURB MEASUREMENTS
RTU DATA | Area Served (LOCATION) EX: Front Sales Pharmacy Storage PARTNER SPACE etc | DATE OF MFG. | EF (ROOF MOUNTED/IN-LINE) | MAKE | MODEL # | SERIAL # | INTERNAL & EXTERNAL UNIT CONDITION COMMENTS & NOTES: (*Give Full Details On Each Unit*) |  | CAPACITY TONS | HEAT TYPE PROPANE / NATURAL GAS / ELECTRIC / HEAT PUMP - AUX HEAT KW | HEATING CAPACITY MAX INPUT(BTU / KW) | LOCATION (UNIT / DUCT) | DUCT LOCATION (SUPPLY / RETURN) | GFI POWERED (Y/N) (BLDG. / RTU) | VOLTAGE (NAMEPLATE) | VOLTAGE (MEASURED) | PHASE | IF NEAREST EDGE OF RTU IS <10' FROM THE EDGE OF THE ROOF PROVIDE DISTANCE BETWEEN THE TWO EDGES (in) | DOES ROOF HAVE A PARAPET? (Y/N) | DOES RTU/HVAC EQUIPMENT UTALIZE OSHA ROOFTOP GUARD RAILS? (Y/N) | EXISTING CURB ADAPTER (YES/NO) | CURB MEASUREMENTS O.D. | UNIT MEASUREMENTS O.D.
RTU 1 | ENTRANCE | NL |  | TRANE | YHC092A3RLA34D | 932100067L | INTERNALS ARE DUSTY BUT NO OBVIOUS DAMAGE. ELECTRICAL COMPRTMENT IS DUSTY. CONDENSER COILS ARE SLIGHTLY DAMAGED. |  | 7.5 | GAS | NL | UNIT | SUPPLY | NO | 208 | 207 | 3 | N/A | YES | NO | NO | 84X50 | 88X52
RTU 2 | SALES FLOOR | NL |  | TRANE | YHC063A3RLA1SD | 932101734L | INTERNALS ARE DUSTY BUT NO OBVIOUS DAMAGE. ELECTRICAL COMPRTMENT IS DUSTY. CONDENSER COILS ARE SLIGHTLY DAMAGED. |  | 5 | GAS | NL | UNIT | SUPPLY | YES | 208 | 206.9 | 3 | N/A | YES | NO | NO | 66X41 | 69X44
RTU 3 | SALES FLOOR | NL |  | TRANE | YCD151C3LKBB | 932100924D | INTERNALS ARE DUSTY BUT NO OBVIOUS DAMAGE. ELECTRICAL COMPRTMENT IS DUSTY. CONDENSER COILS ARE SLIGHTLY DAMAGED. CONDENSATE DRAIN MELTED |  | 12.5 | GAS | 150000 | UNIT | SUPPLY | NO | 208 | 207 | 3 | N/A | YES | NO | NO | 103X67 | 107X71
RTU 4 | PHARMACY | NL |  | TRANE | YHC063A3RLA1SD | 932101437L | INTERNALS ARE DUSTY BUT NO OBVIOUS DAMAGE. ELECTRICAL COMPRTMENT IS DUSTY. CONDENSER COILS ARE SLIGHTLY DAMAGED. |  | 5 | GAS | NL | UNIT | SUPPLY | YES | 208 | 206.9 | 3 | N/A | YES | NO | NO | 66X41 | 69X44
RTU 5 | SALES FLOOR | NL |  | TRANE | YHC033A3RLA1TD | 932100276L | INTERNALS ARE DUSTY BUT NO OBVIOUS DAMAGE. ELECTRICAL COMPRTMENT IS DUSTY. CONDENSER COILS ARE SLIGHTLY DAMAGED. CONDENSATE DRAIN BROKEN |  | 2.5 | GAS | NL | UNIT | SUPPLY | NO | 208 | 207.6 | 3 | N/A | YES | NO | NO | 66X42 | 69X45
RTU 6 | BACK OF HOUSE | NL |  | TRANE | YHC033A3RLSA1TD | 932100262L | INTERNALS ARE DUSTY BUT NO OBVIOUS DAMAGE. ELECTRICAL COMPRTMENT IS DUSTY. CONDENSER COILS ARE SLIGHTLY DAMAGED. |  | 2.5 | GAS | NL | UNIT | SUPPLY | YES | 208 | 206.8 | 3 | N/A | YES | NO | NO | 66X43 | 69X44
RTU 7
EH
SPLIT SYSTEM DATA
CU 1 | N/A | [5 empty] | *include line set sizes*
CU 2 | N/A | [5 empty] | *include line set sizes*
CU 3 | N/A | [5 empty] | *include line set sizes*
AHU 1 | N/A
AHU 2 | N/A
AHU 3 | N/A
EVAPORATIVE COOLER/SWAMP COOLER | N/A
VENTILATION DATA
ERV 1
ERV 2
STOCK ROOM SF
STOCK ROOM EF
EF 1 | BREAK ROOM | 2009-07-01 | ROOF MOUNTED | COOK | 100ACFH | 287SC73250 | DUSTY INSIDE OF CAP | [7 empty] | 115 | NA | 1 |  |  |  | NO | 18X18 | 18X18
EF 2 | RESTROOMS | 2009-07-01 | ROOF MOUNTED | COOK | 100ACFH | 287SC73250 | DUSTY INSIDE OF CAP | [7 empty] | 115 | NA | 1 |  |  |  | NO | 18X19 | 18X19
EF 3
EF 4
EF 5
EF 6
EF 7
General Store Notes | [6 empty] | Electrical Panel Information | FUSED SWITCH OR BREAKER | FUSE / BREAKER BRAND | FUSE / BREAKER MODEL # | RATING(AMPS) | WIRE SIZE | CONDUIT SIZE AT UNIT
Former Rite Aid (Y/N): | [6 empty] | RTU-1 | FUSED SWITCH | TRINIC | TRS50R | 50A | 6AWG | 1.5"
Partner Tenant (included but not lmited to: ex. Village Medical (VMD), LabCorp, Novant, and MedExpress) | NO |  | Provid partner name |  |  |  | RTU-2 | FUSED SWITCH | INDICATOR | IDSR45 | 45A | 8AWG | 1.5"
If Partner Tenant Exists do they have full height walls? (Y/N) | N/A |  | Full height walls are defined as walls up to ceiling. |  |  |  | RTU-3 | FUSED SWITCH | TRINIC | TRS80R | 80A | 4AWG | 1.5"
Obvious "non-typical" Heat Load (Y/N) provide detail in note section | NO |  | Ex.: Floor to glass windows, Sky Lights, Permanent Heat Productin Displays, Etc (please make high level note of any potential items.) |  |  |  | RTU-4 | FUSED SWITCH | INDICATOR | IDSR45 | 45A | 8AWG | 1.5"
Tenant Space (Y/N): | NO |  | Tenant Name (VMD/Kroger/LabCorp, etc.): |  |  |  | RTU-5 | FUSED SWITCH | TRINIC | TRS30R | 30A | 10AWG | 1.5"
Photo Lab (Y/N): | YES |  | Dry/Wet Lab: |  |  |  | RTU-6 | BREAKER | SQUARE D | HU361RB | 30A | 8AWG | 1.5"
Roof Condition (Good/Fair/Poor): | GOOD | [5 empty] | RTU-7 | N/A
Ductwork Type (Galvanized, Duct Board, Sock Duct, Other) | GALVANIZED |  | If "Other" Specify Type: |  |  |  | RTU-8 | N/A
Unit Hail Damage (Y/N): | YES | [5 empty] | CU 1 | N/A
Store within 20 Miles of Ocean? (Y/N): | NO | [5 empty] | CU 2 | N/A
Existing EMS (Y/N): | YES |  | EMS Type(FSG/Gridpoint): |  |  |  | CU 3 | N/A
Fire Alarm Panel Operational (Y/N): | YES |  | Panel Model#: |  |  |  | AHU 1 | N/A
Photo of Fire Alarm Panel Taken (Y/N): | [6 empty] | AHU 2 | N/A
Main Refrigeration Type (Remote Condensing Unit or Self-Contained) | REMOTE | [5 empty] | AHU 3 | N/A
Main Refridgeration Type (Walk-In or Reach-In) | Freezer: |  | REACH IN |  |  |  | EVAPORATIVE COOLER/SWAMP COOLER | N/A
| Cooler: |  | REACH IN |  |  |  | STOCK ROOM SF | N/A
Self-Contained Refrigeration ONLY Door Count: | Freezer: | [5 empty] | STOCK ROOM EF | N/A
Cooler:
Obvious Visual Damage to MDP (Y/N): | NO |  | Explain Visual Damage:
Notes for Installer:
Original Curb Dimensional Data
RTU# | RTU1 | RTU2 | RTU3 | RTU4 | RTU5 | RTU6 | RTU7 | EH
Curb Type | 2 | 2 | 2 | 2 | 2
A (Length) | 84" | 66" | 103" | 66" | 66" | 66"
B (Width) | 50" | 41" | 67" | 41" | 41" | 41"
E | 18" | 16" | 25" | 16" | 14" | 14"
F | 18" | 16" | 18" | 16" | 16" | 16"
G | 34" | 18" | 52" | 18" | 24" | 24"
H | NA | NA | NA | NA | NA | NA
I | 2" | 2" | 4" | 2" | 2" | 2"
J | 16" | 16" | 5" | 16" | 16" | 16"
K | 3" | 3" | 6" | 3" | 3" | 3"
L | N/A | N/A | N/A | 0/ | N/A | N/A
M
N
O