## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9000 | 8532 | 7200 | 6700 | 1800 | 1832 | 20% | 21.47%
AC-2 | DINNING A/MECH/RR | 3020 | 3152 | 2340 | 2484 | 680 | 668 | 22.52% | 21.19%
AC-3 | DINNING A/DT/ORDER | 6000 | 6236 | 5000 | 5213 | 1000 | 1023 | 16.67% | 16.4%
AC-4 | DINNING B/ ENTRY | 2765 | 2760 | 2135 | 2113 | 630 | 647 | 22.78% | 23.44%
AC-5 | PLAY AREA | 1800 | 1895 | 1500 | 1604 | 300 | 291 | 16.67% | 15.36%
AC-6 | MULTI-PURPOSE | 1200 | 1186 | 1000 | 980 | 200 | 206 | 16.67% | 17.37%
EF-1 | HD 1 | [10 empty] | 1913 | 1886
EF-2 | HD 2 | [10 empty] | 701 | 719
EF-3 | RESTROOM | [12 empty] | 450 | 465
EF-4 | HD 3 | [10 empty] | 701 | 730
EF-5
TOTALS |  | 23785 | 23761 | 19175 | 19094 | 4610 | 4667 |  |  | 0 | 0 | 3315 | 3335 | 450 | 465
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4610 | 4667 |  | FRONT |  | 0.0171 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3765 | 3800 |  | SIDE |  | 0.0169 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 845 | 867 |  | REAR |  | 0.0158 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0166 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390