## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
DOAS1 |  | 3550 | 3515 | 0 | 0 | 3550 | 3515 | 100% | 100%
RTU1 |  | 5500 | 5016 | 4350 | 3765 | 1150 | 1251 | 20.91% | 24.94%
KEF-1 | [11 empty] | 2375 | 2265
KEF-2 | [11 empty] | 1375 | 1312
EF-1 | [13 empty] | 150 | 43
EF-2 | [13 empty] | 150 | 37
EF-3 | [13 empty] | 150 | 31
TOTALS |  | 9050 | 8531 | 4350 | 3765 | 4700 | 4766 |  |  | 0 | 0 | 3750 | 3577 | 450 | 111
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4700 | 4766 |  | FRONT |  | 0.0075 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4200 | 3688 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 500 | 1078 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0075 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0