## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | CORE | 3400 | 3390 | 2900 | 2882 | 500 | 508 | 14.71% | 14.99%
RTU-2 | DELI | 5000 | 4996 | 4300 | 4307 | 700 | 689 | 14% | 13.79%
RTU-3 | RETAIL | 3000 | 3010 | 2750 | 2761 | 250 | 249 | 8.333% | 8.272%
EF-1 | RR/FOOD | [12 empty] | 950 | 877
EF-2 | WATER SERVICE RM | [12 empty] | 60 | 61
TOTALS |  | 11400 | 11396 | 9950 | 9950 | 1450 | 1446 |  |  | 0 | 0 | 0 | 0 | 1010 | 938
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1450 | 1446 |  | FRONT |  | 0.0128 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1010 | 938 |  | SIDE |  | 0.0016 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 440 | 508 |  | REAR |  | 0.0029 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0057667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0