## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 1600 | 1701 | 1450 | 1540 | 150 | 161 | 9.375% | 9.465%
RTU-2 | KITCHEN | 1600 | 1626 | 1450 | 1469 | 150 | 157 | 9.375% | 9.656%
RTU-3 | DINING | 1600 | 1694 | 1285 | 1359 | 315 | 335 | 19.69% | 19.78%
RTU-4 | DINING | 1500 | 1586 | 1190 | 1290 | 310 | 296 | 20.67% | 18.66%
MUA-1 | COOKLINE | [8 empty] | 1976 | 2011
EF-1 | KITCHEN HD | [10 empty] | 2381 | 2460
EF-2 | RESTROOM | [12 empty] | 75 | 95
EF-3 | RESTROOM | [12 empty] | 75 | 97
TOTALS |  | 6300 | 6607 | 5375 | 5658 | 925 | 949 |  |  | 1976 | 2011 | 2381 | 2460 | 150 | 192
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2901 | 2960 |  | FRONT |  | 0.0058 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2531 | 2652 |  | SIDE |  | 0.0052 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 370 | 308 |  | REAR |  | 0.0046 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0052 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0