## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3067 | 2673 | 2300 | 1972 | 767 | 701 | 25.01% | 26.23%
RTU-2 | DINING 1 | 1600 | 1623 | 1200 | 1211 | 400 | 412 | 25% | 25.39%
RTU-3 | DINING 2 | 1600 | 1593 | 1200 | 1167 | 400 | 426 | 25% | 26.74%
MUA-1 | [9 empty] | 2168 | 2168
EF-1 | [11 empty] | 3563 | 3563
EF-2 | [13 empty] | 159 | 159
TOTALS |  | 6267 | 5889 | 4700 | 4350 | 1567 | 1539 |  |  | 2168 | 2168 | 3563 | 3563 | 159 | 159
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3735 | 3707 |  | FRONT |  | -0.0046 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 3722 | 3722 |  | SIDE |  | -0.0061 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 13 | -15 |  | REAR |  | -0.003 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0045667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
BALANCE SCHEDULE CONTINGENT ON CLEAN MUA INTAKE FILTERS AND CLEAN RTU OA INTAKE FILTERS
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0