## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5000 | 4791 | 4250 | 4012 | 750 | 779 | 15% | 16.26%
DOAS-1 | KITCHEN | 2900 | 2279 | -200 | 0 | 3100 | 2279 | 106.9% | 100%
KEF-1 | GRIDDLE | [10 empty] | 1700 | 1730
KEF-2 | FRYER | [10 empty] | 775 | 782
EF-1 | RR | [12 empty] | 150 | 72
TOTALS |  | 7900 | 7070 | 4050 | 4012 | 3850 | 3058 |  |  | 0 | 0 | 2475 | 2512 | 150 | 70
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3850 | 3058 |  | FRONT |  | 0.0187 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2625 | 2582 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1225 | 476 |  | REAR |  | 0.0179 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0183 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
DOAS Reduced to prevent over pressurization of the building.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0