## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | SALES | 5250 | 5158 | 4525 | 4452 | 725 | 706 | 13.81% | 13.69%
RTU-2 | SALES | 3500 | 3417 | 2850 | 2796 | 650 | 621 | 18.57% | 18.17%
RTU-3 | PHARMACY | 1750 | 1829 | 1650 | 1829 | 100 | 0 | 5.714% | 0%
EF-2 | LOUNGE | [12 empty] | 300 | 160
EF-3 | MENS RR | [12 empty] | 200 | 195
EF-4 | WOMENS RR | [12 empty] | 200 | 185
EF-5 | OFFICE | [12 empty] | 300 | 0
TOTALS |  | 10500 | 10404 | 9025 | 9077 | 1475 | 1327 |  |  | 0 | 0 | 0 | 0 | 1000 | 540
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 1475 | 1327 |  | FRONT |  | 0.006 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1000 | 540 |  | SIDE |  | - |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 475 | 787 |  | REAR |  | - | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.006 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
RTU-3 OUTSIDE AIR DAMPER KEPT CLOSED PER EOR TO AID IN KEEPING SPACE HUMIDITY WITHIN ACCEPTABLE LEVEL.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0