## ERV (1)
National TAB
Project: NCANG Repair Bldg 51
Address: 4930 Minuteman Way Charlotte, NC
Asset: ERV
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | Greenheck |  | Manufacturer | Greenheck
Model Number | RVE-85-52D-0-J-D1 |  | Model Number | RVE-85-52D-0-J-D1
Serial Number |  |  | Serial Number
No. Pre Filters / Size
No. Pre Filters / Size
Motor Data |  |  | Motor Data
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 5.0 / 1760 |  | Horsepower / RPM | 5.0 / 1760
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 5600 |  | Total CFM | 5600
Fan RPM | 1545 |  | Fan RPM | 1466
VFD Speed | 52.7 |  | VFD Speed | 50
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 3.94 |  | Motor B.H.P. | 3.40
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 2.65 |  | Total SP | 2.04
Heat Wheel P.D. | 1.42 |  | Heat Wheel P.D. | 1.54
Heating P.D. | 0.38 |  | Total ESP | 0.50
Pre Filters P.D. | 0.29
Total ESP | 0.50
EAT Summer DB / WB | 94.1/77.1 |  | EAT Summer DB | 75.0
LAT Summer DB / WB | 81.2/68.1 |  | LAT Summer DB / WB | 87.8/72.5
EAT Winter DB / WB | 20.5/17.0 |  | EAT Winter DB | 72.0
LAT Winter DB / WB | 53.4/43.6 |  | LAT Winter DB / WB | 37.7/33.1

## ERV-1 AIR DEV
National TAB
Project: NCANG Repair Bldg 51
Address: 4930 Minuteman Way Charlotte, NC
Asset: ERV-1 AIR DEVICES
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
REE1-1 | H145 | RG-4 | 30X18 | 2050 |  |  | 0
REE1-2 | H145 | RG-4 | 30X18 | 2050 |  |  | 0
REE1-3 | H134 | RG-2 | 36X12 | 1500 |  |  | 0
RETURN |  |  |  | 5600 |  | 0 | 0
EE1-1 | H145 | SG-5 | 18X14 | 1025 |  |  | 0
EE1-2 | H145 | SG-5 | 18X14 | 1025 |  |  | 0
EE1-3 | H134 | SG-6 | 12X10 | 500 |  |  | 0
EE1-4 | H134 | SG-6 | 12X10 | 500 |  |  | 0
EE1-5 | H134 | SG-6 | 12X10 | 500 |  |  | 0
EE1-6 | H145 | SG-5 | 18X14 | 1025 |  |  | 0
EE1-7 | H145 | SG-5 | 18X14 | 1025 |  |  | 0
SUPPLY |  |  |  | 5600 |  | 0 | 0

## ERV (2)
National TAB
Project: NCANG Repair Bldg 51
Address: 4930 Minuteman Way Charlotte, NC
Asset: ERV
Supply Side |  |  | Exhaust Side
Unit Data |  |  | Unit Data
Manufacturer | Greenheck |  | Manufacturer | Greenheck
Model Number | RVE-85-52D-0-J-D1 |  | Model Number | RVE-85-52D-0-J-D1
Serial Number |  |  | Serial Number
No. Pre Filters / Size
No. Pre Filters / Size
Motor Data |  |  | Motor Data
Motor MFG / Frame |  |  | Motor MFG / Frame
Horsepower / RPM | 5.0 / 1760 |  | Horsepower / RPM | 5.0 / 1760
Rated Volts / Phase | 460 / 3 |  | Rated Volts / Phase | 460 / 3
Rated Amperage / SF |  |  | Rated Amperage / SF
Test Data |  |  | Test Data
| Design | Actual |  | Design | Actual
Total CFM | 5600 |  | Total CFM | 5600
Fan RPM | 1545 |  | Fan RPM | 1466
VFD Speed | 52.7 |  | VFD Speed | 50
RL Voltage | 460 |  | RL Voltage | 460
RL Amperage |  |  | RL Amperage
Motor B.H.P. | 3.94 |  | Motor B.H.P. | 3.40
Performance Data |  |  | Performance Data
| Design | Actual |  | Design | Actual
Suction S.P. |  |  | Suction S.P.
Discharge S.P. |  |  | Discharge S.P.
Total SP | 2.65 |  | Total SP | 2.04
Heat Wheel P.D. | 1.42 |  | Heat Wheel P.D. | 1.54
Heating P.D. | 0.38 |  | Total ESP | 0.50
Pre Filters P.D. | 0.29
Total ESP | 0.50
EAT Summer DB / WB | 94.1/77.1 |  | EAT Summer DB | 75.0
LAT Summer DB / WB | 81.2/68.1 |  | LAT Summer DB / WB | 87.8/72.5
EAT Winter DB / WB | 20.5/17.0 |  | EAT Winter DB | 72.0
LAT Winter DB / WB | 53.4/43.6 |  | LAT Winter DB / WB | 37.7/33.1

## ERV-2 AIR DEV
National TAB
Project: NCANG Repair Bldg 51
Address: 4930 Minuteman Way Charlotte, NC
Asset: ERV-2 AIR DEVICES
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
REE2-1 | H117 | RG-3 | 20X24 | 1900 |  |  | 0
REE2-2 | H117 | RG-3 | 20X24 | 1900 |  |  | 0
REE2-3 | H117 | RG-3 | 20X24 | 1900 |  |  | 0
RETURN |  |  |  | 5700 |  | 0 | 0
EE2-1 | H114 | SG-5 | 18X14 | 1000 |  |  | 0
EE2-2 | H114 | SG-5 | 18X14 | 1000 |  |  | 0
EE2-3 | H114 | SG-5 | 18X14 | 1000 |  |  | 0
EE2-4 | H114 | SG-5 | 18X14 | 1000 |  |  | 0
EE2-5 | H114 | SG-5 | 18X14 | 800 |  |  | 0
EE2-6 | H114 | SG-5 | 18X14 | 800 |  |  | 0
SUPPLY |  |  |  | 5600 |  | 0 | 0