Shake Shack – Lee’s Summit, MO Commissioning Kick-Off Meeting

Collaboration & Communication

- Kick off meeting [July 22nd, 2021]

  - What is commissioning:  Process to assure all systems and components are designed, installed, operating, and perform to the owner requirements

    - CxA - Design Review validate owner Requirements

    - CxA - Intermediate commissioning FIV to validate each systems route, size, material, and installation details ensure capacity, access, and longevity

    - Sub-Contractor Pre-Commissioning checklist validate components in each system are as specified/approved, installed, and functional per design, OEM, and local AHJ requirements

    - CxA - Final Commissioning activities validate final function, SOO, and performance per owner requirements

- Team identification and roles

  - Owner - CxA

    - General Contractor - CxA

      - Mechanical & TAB team - CxA

      - Fire Sprinkler / Fire suppression - CxA

      - Plumbing - CxA

      - Electrical - CxA

      - Lighting - CxA

- Support [OEM’S & AEC team]

  - Schnackel Engineers

  - Halton Kitchen Hoods

  - Carrier RTU’s

  - Trimark Kitchen Equipment

  - Lutron lighting

  - Noritz water heaters

  - National TAB Commissioning Team

Schedule of Events:

- Weekly GC meetings

- Underground Plumbing and Electrical Inspection [Approx.:  7-26-2021 by CxA]

- In-Wall inspection [TBD – by CxA]

- Above-Ceiling inspection [TBD – by CxA]

  - Issue/RFI resolution Process:  GC/Sub-Contractor &  Support Team

    - RFI:  Condition cannot be met, Local AHJ supersedes Design.

    - Issue:  Condition not installed, operating as designed

- Final Commissioning Readiness Requirements [TBD – by GC/Sub-Contractor]

- Startup Reports

- Completed Pre-Commissioning Checklist

- TAB report

- City Inspection Reports (GC)

Final Commissioning Activities [Last week prior to Turn Over – CxA]

- Pass/Fail

  - Fail – Issue Resolution by division Sub-Contractor

- Warranty documents, O&M’s, Equipment Tags

- Owner Training

- Final Commissioning Report

Field Installation Verification:  Specified Materials, Routing, Size, Supports

- CxA will perform field verification of details for underground, in-wall, and above ceiling inspections

  - Review will consist of division specified materials, routing, size, supports, installation details

  - Issues or RFI’s will be sent if omissions, errors, or change request are identified

  - GC/Trade should respond no later than 5 business days with resolution or clarification response

  - Engineer/Owner may review for acceptance any requested change

Pre-Commissioning Checklist of specified equipment:

Division specific checklist will be sent to each responsible Sub-Contractor for review of required checklist.  Each Sub-Contractor is to review and accept or revise as necessary the checklist to ensure it accurately reflects their scope, installation details, and local AHJ code requirements.  CxA will setup a quick review meeting with each of the following contractors to review the mark-ups and resubmit final pre-commissioning checklist.

Each Checklist will be organized in a similar manner:

- Identification:  Matches accepted submittal data

- Installation details:  Installed per MFG requirements, design details, and local code

- Operation:  Normal and abnormal interlocks and operation

  - Startup reports to be collected

  - City inspection reports to be collected

  - Specialized testing

  - GC – Owner authorized installation certificate of installation

Completed checklist are due prior to final commissioning is to be scheduled.

Functional Performance testing:

To be completed by the commissioning agent.

- Review all completed checklist

- Ensure all open issues / RFI’s created during the processes have been resolved

- TAB has been completed

Overview:  Each divisional contractor to be available / present on site during their scheduled test period.  Anticipate 1-2 hours, but in some cases, this may be reduced based on previous inspections, city test, startups, and functional verifications.

Electrical (General scope)

- Ensure all circuit power is connected to correct appliances

- Demonstrate panel A,B,C balance phase Loads

- Test all GFCI outlets

- Validate timers are set correctly and are functional

- Validate starter/overloads size, settings, and interlocks

- Validate emergency back-up systems/power

- Review SOO of normal and abnormal operation and validate interlocks

Sprinkler (General scope)

- Tamper Valves

- Test Drain

- Flow switch

- Dry Valve – Compressor settings and operation

- Sprinkler Head installation hazard zones and types

- Abnormal alarms, lights, and signals

Plumbing (General scope)

- Test all gas line pressures at appliances (100% maximum load)

- Validate all external regulator pressure settings

- Test gravity drain primers

- Test all water heater safety devices and settings

- Validate sequence of operation of the recirculated hot water/hot water heater system

- Test mixing Valve – sink hot water heater temperatures and time

- Review for abnormal sound or vibration

HVAC (General scope)

- TAB report completed

- RTU settings, thermostat programming, sensor calibration

- RTU coil/Exchanger performance EAT/LAT conditions

- Refrigeration and gas heat operation

- Free cooling enthalpy sensors and SOO

- unoccupied, occupied operation

- CO2 ppm operation

- Dehumidification performance

- Fire suppression & smoke detector interlocks – RTU shutdown

- Hood capture test

- Building pressure

- Space performance manual & automatic control

- Review for abnormal sound or vibration

Lighting

- Startup

- Programming

- Validate SOO (automatic and manual)

- Measure Space lighting