## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 8872 | 7000 | 7201 | 1750 | 1671 | 20% | 18.83%
AC-2 | SERVING | 5250 | 5268 | 4350 | 4409 | 900 | 859 | 17.14% | 16.31%
AC-3 | DINING | 5250 | 5400 | 3650 | 3818 | 1600 | 1582 | 30.48% | 29.3%
AC-4 | BOH | 1875 | 1921 | 1375 | 1380 | 500 | 541 | 26.67% | 28.16%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1913 | 1991
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1436
EF-3 | RESTROOM | [12 empty] | 375 | 376
TOTALS |  | 21125 | 21461 | 16375 | 16808 | 4750 | 4653 |  |  | 0 | 0 | 3315 | 3427 | 375 | 376
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4750 | 4653 |  | FRONT |  | 0.0035 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3690 | 3803 |  | SIDE |  | 0.008 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1060 | 850 |  | REAR |  | 0.0064 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0059667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
[1] Not all ceiling tiles in place at time of TAB. Final Building pressure expected to be higher.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390