## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 1800 | 1735 | 1305 | 1370 | 495 | 365 | 27.5% | 21.04%
RTU-2 | DINING | 5000 | 5064 | 4078 | 4157 | 922 | 907 | 18.44% | 17.91%
RTU-3 | DINING | 5000 | 5099 | 4078 | 4136 | 922 | 963 | 18.44% | 18.89%
RTU-4 | KITCHEN | 5000 | 5151 | 4000 | 5151 | 1000 | 0 | 20% | 0%
MUA-1 | KITCHEN | [8 empty] | 5845 | 4819
KEF-1 | HOOD1 | [10 empty] | 3575 | 3521
KEF-2 | HOOD2 | [10 empty] | 1610 | 1747
KEF-3 | HOOD3 | [10 empty] | 1943 | 1876
EF-1 | RESTROOM | [12 empty] | 150 | 0
EF-2 | RESTROOM | [12 empty] | 200 | 80
EF-3 | RESTROOM | [12 empty] | 50 | 51
TOTALS |  | 16800 | 17049 | 13461 | 14814 | 3339 | 2235 |  |  | 5845 | 4819 | 7128 | 7144 | 400 | 131
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 9184 | 7054 |  | FRONT |  | -0.012 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 7528 | 7275 |  | SIDE |  | -0.006 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1656 | -221 |  | REAR |  | -0.004 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0073333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0