## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | RETAIL | 3000 | 0 | 2490 | 0 | 510 | 0 | 17% | #DIV/0!
RTU-2 | FOOD SERVICE | 4000 | 3916 | 3320 | 3219 | 680 | 697 | 17% | 17.8%
RTU-3 | RETAIL | 2000 | 1998 | 1660 | 1654 | 340 | 344 | 17% | 17.22%
EF-1 | [13 empty] | 370 | 364
EF-2 | [13 empty] | 70 | 95
EF-3 | [13 empty] | 100 | 96
EF-4 | [13 empty] | 800 | 782
TOTALS |  | 9000 | 5914 | 7470 | 4873 | 1530 | 1041 |  |  | 0 | 0 | 0 | 0 | 1340 | 1337
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 1530 | 1041 |  | FRONT |  | -0.0087 | [8 empty] | TRUE | TRUE | TRUE
TOTAL EXHAUST |  | 1340 | 1337 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 190 | -296 |  | REAR |  | -0.0078 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.00825 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0