## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 5200 | 5470 | 4300 | 4616 | 900 | 854 | 17.31% | 15.61%
RTU-2 | KITCHEN | 5000 | 4827 | 4050 | 3941 | 950 | 886 | 19% | 18.36%
RTU-OA | RTU 1& 2 | 3250 | 3318 | 1250 | 1120 | 2000 | 2198 | 61.54% | 66.24%
PRV-2 | HOOD 2 | [10 empty] | 1500 | 1572
PRV-3 | HOOD 1 | [10 empty] | 1500 | 1591
PRV-4 | HOOD 3 | [10 empty] | 350 | 380
EF-1 | RESTROOM | [12 empty] | 220 | 215
EF-2 | MOP ROOM | [12 empty] | 50 | 48
EF-3 | RESTROOM | [12 empty] | 70 | 68
TOTALS |  | 13450 | 13615 | 9600 | 9677 | 3850 | 3938 |  |  | 0 | 0 | 3350 | 3543 | 340 | 331
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3850 | 3938 |  | FRONT |  | 0.0017 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3690 | 3874 |  | SIDE |  | 0.0013 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 160 | 64 |  | REAR |  | 0.0041 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0023667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0