## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4000 | 3947 | 2150 | 2066 | 1850 | 1881 | 46.25% | 47.66%
RTU-2 | DINING/RR | 3980 | 4145 | 2130 | 2272 | 1850 | 1873 | 46.48% | 45.19%
DOAS-1 | KITCHEN | 4000 | 4135 | 300 | 263 | 3700 | 3872 | 92.5% | 93.64%
MUA-1 | COOKLINE/SF GRILL | [8 empty] | 3200 | 3294
KEF-H1L | COOKLINE | [10 empty] | 1425 | 1327
KEF-H1R | COOKLINE | [10 empty] | 1425 | 1327
KEF-3 | SF GRILL | [10 empty] | 3360 | 3217
KEF-H4 | PREP | [10 empty] | 2340 | 2209
EF-DISH | DISH | [10 empty] | 800 | 673 |  |  | TRUE | FALSE | FALSE
TEF-1 | TOILETS | [12 empty] | 200 | 200
TOTALS |  | 11980 | 12227 | 4580 | 4601 | 7400 | 7626 |  |  | 3200 | 3294 | 9350 | 8753 | 200 | 200 | #DIV/0! | #DIV/0! | FALSE
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | #DIV/0!
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 10600 | 10920 |  | FRONT
TOTAL EXHAUST |  | 9550 | 8953 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 1050 | 1967 |  | REAR
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0