## Sheet1
National TAB
Project: MD0055ZZ, G.H. FALLON FED BUILDING (BALTIMORE, MD)
ASHRAE 62.1 Minimum Ventilation Rates
[10 empty] | Occupancy Category | CFM/Person | CFM/Sqft
Air Handling Units | [9 empty] | Office Building | 5 | 0.06
UNIT | Area Served | Space Type(s) Served | Sq Ft of Serviced Area | Occupant Population | SUPPLY CFM |  | HVAC RETURN |  | OUTDOOR Air CFM |  | Ashrae 62.1 calculated ventilation Rates (CFM) | Notes | Do not show - Formula reference only
[5 empty] | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | Lobby 16 - 9 and Tenant 8 - 3 | Common/ Office Areas | 138540 | 811 | 24960 |  | 0 |  | 24960 |  | 12367.4 |  | 12367.4
AHU-2 | Tenant 16 - 9 and Lobby 8 - 3 | Common/ Office Areas | 154625 | 1001 | 34000 |  | 0 |  | 34000 |  | 14282.5 |  | 14282.5
AHU-3 | O.A. to AHUs on East Side B - 2nd |  | n/a | 677 | 21750 |  | 0 |  | 21750 |  | #VALUE! | #VALUE! | #VALUE!
AHU-4 | 1st FL West |  | 21190 | 77 | 21740 |  | 17440 |  | 4300 |  | 1656.4 |  | 1656.4
AHU-5 | 1st and 2nd Fl Lobby |  | 22335 | 10 | 11000 |  | 8450 |  | 2550 |  | 1390.1 |  | 1390.1
AHU-6 | 1st Fl East |  | 11830 | Supl. AHU | 11000 |  | 8700 |  | 2300 |  | #VALUE! | #VALUE! | #VALUE!
AHU-7 | 2nd Fl East |  | 11920 | Supl. AHU | 12500 |  | 9900 |  | 2600 |  | #VALUE! | #VALUE! | #VALUE!
AHU-8 | 2nd Fl West |  | 20590 | Supl. AHU | 18500 |  | 15080 |  | 3420 |  | #VALUE! | #VALUE! | #VALUE!
AHU-9 | O.A. to AHUs West G and 2nd Fl |  | n/a | 319 | 13650 |  | 0 |  | 13650 |  | #VALUE! | #VALUE! | #VALUE!
AHU-10 | IRS MTS and TAC |  | 11425 | Supl. AHU | 11000 |  | 8800 |  | 2200 |  | #VALUE! | #VALUE! | #VALUE!
AHU-11 | Ground Fl. North West ( VA O.I.G. ) |  | 9115 | Supl. AHU | 6000 |  | 4820 |  | 1180 |  | #VALUE! | #VALUE! | #VALUE!
AHU-12 | DHS CIS Fingerprint |  | 4810 | Supl. AHU | 2800 |  | 1870 |  | 930 |  | #VALUE! | #VALUE! | #VALUE!
AHU-13 | Ground Fl. West (V.A. Conference) |  | 2215 | Supl. AHU | 1800 |  | 1160 |  | 640 |  | #VALUE! | #VALUE! | #VALUE!
AHU-14 | Fitness Center |  | 5075 | Supl. AHU | 4500 |  | 2600 |  | 1900 |  | #VALUE! | #VALUE! | #VALUE!
AHU-15 | Day Care Center/Credit Union |  | 10550 | Supl. AHU | 8600 |  | 6600 |  | 2000 |  | #VALUE! | #VALUE! | #VALUE!
AHU-16 | West Building Conference Rooms |  | 9085 | Supl. AHU | 6800 |  | 5480 |  | 1320 |  | #VALUE! | #VALUE! | #VALUE!
AHU-17 | Ground Fl. South Central (Café Area) |  | 7015 | Supl. AHU | 9000 |  | 5100 |  | 3900 |  | #VALUE! | #VALUE! | #VALUE!
AHU-18 | South VBA Class Rooms 2-6 |  | 10690 | Supl. AHU | 10500 |  | 7400 |  | 3100 |  | #VALUE! | #VALUE! | #VALUE!
AHU-19 | Ground Fl. East Corridor and V.B.A. |  | 8965 | Supl. AHU | 9500 |  | 7500 |  | 2000 |  | #VALUE! | #VALUE! | #VALUE!
AHU-20 | VBA Offices/Class 1 & Pass. Elevator Lobby |  | 11915 | Supl. AHU | 8700 |  | 6300 |  | 2400 |  | #VALUE! | #VALUE! | #VALUE!
AHU-21 | Basement VBA Space East of Roadway |  | 9450 | Supl. AHU | 10000 |  | 6900 |  | 3100 |  | #VALUE! | #VALUE! | #VALUE!
AHU-22 | Basement Main Transformer Rooms |  | 3035 | NA | 8000 |  | 8000 |  |  |  | #VALUE! | #VALUE! | #VALUE!
AHU-23 | Upper Garage West, Lower NW |  | 27310 | NA | 52000 |  | 0 |  | 52000 |  | #VALUE! | #VALUE! | #VALUE!
AHU-24 | Garage |  | 10965 | NA | 52000 |  | 0 |  | 52000 |  | #VALUE! | #VALUE! | #VALUE!
AHU-25 | Loading Dock & Rooms |  | 5220 | NA | 8000 |  | 0 |  | 8000 |  | #VALUE! | #VALUE! | #VALUE!
AHU-24 USMS | USMS Space in Basement |  | 8777 | 10 |  |  |  |  | 1500 |  | 576.62 |  | 576.62
[11 empty] | Occpuancy & Sqft Area Information Required | [2] | 0
[11 empty] | Occpuancy & Sqft Area Information Required | [2] | 0
[11 empty] | Occpuancy & Sqft Area Information Required | [2] | 0
[11 empty] | Occpuancy & Sqft Area Information Required | [2] | 0
0
[1] | Design Outdoor Air CFM is less than ASHRAE Minimum Ventilation Rates based on occupancy and areas served information. Recommend adjusting and balancing to achieve ventilation airflow quantities.
0
[2] | Actual measured outdoor air CFM is less than ASHRAE minimum. Recommend testing, adjusting, and balancing to achieve optimum air flow rates. | [11 empty] | 0
0
[3] | Information not provided. Requesting information for the Occupancy Population and Sqft of serviced area. Population and sqft area must be provided to draw accurate conclusions and to compate ventilation rates to design and actual measurements. | [11 empty] | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
Note on J11: ====== ID#AAAASv_6iwc (2021-12-03 14:54:55) Original 24,960 - Rebalanced as part of ESPC -David Pule - 3PCC-C
Note on J12: ====== ID#AAAASv_6iwg (2021-12-03 14:54:55) Original 34,000 rebalanced as part of ESPC -David Pule - 3PCC-C
Note on J13: ====== ID#AAAASv_6iwI (2021-12-03 14:54:55) AHU-3 is a Variable Volume D.O.A.S. serving AHUs 6,7,10,17,18,19,20,21 Max volume is 21,750 when all AHUs running -David Pule - 3PCC-C
Note on J19: ====== ID#AAAASv_6iwE (2021-12-03 14:54:55) AHU-9 is a Variable Volume D.O.A.S. serving AHUs 8,11,12,13,14,15,16, and Basement FCUs 2,3,4,5 Max volume is 13,650 with all units running -David Pule - 3PCC-C