## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8125 | 8270 | 6375 | 6437 | 1750 | 1833 | 21.54% | 22.16%
AC-2 | DRIVE THRU | 4375 | 4344 | 3300 | 3238 | 1075 | 1106 | 24.57% | 25.46%
AC-3 | DINNING /RR | 5250 | 5369 | 3975 | 4065 | 1275 | 1304 | 24.29% | 24.29%
AC-4 | BOH | 1750 | 1779 | 1325 | 1353 | 425 | 426 | 24.29% | 23.95%
AC-5 | PLAY AREA |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 | BOH |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HD 1 | [10 empty] | 1913 | 1803
EF-2 | HD 2 & 3 | [10 empty] | 1402 | 1424
EF-3 | RESTROOMS | [12 empty] | 300 | 305
EF4 | RESTROOMS | [12 empty] | 140 | 131
TOTALS |  | 19500 | 19762 | 14975 | 15093 | 4525 | 4669 |  |  | 0 | 0 | 3315 | 3227 | 440 | 436
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4525 | 4669 |  | FRONT |  | 0.0146 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3755 | 3663 |  | SIDE |  | 0.0132 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 770 | 1006 |  | REAR |  | 0.009 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.012267 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390