## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4850 | 4911 | 3850 | 3891 | 1000 | 1020 | 20.62% | 20.77%
DOAS-1 | KITCHEN | 2650 | 2497 | 0 | 0 | 2650 | 2497 | 100% | 100%
KEF-1 | GRIDDLE | [10 empty] | 1700 | 1603
KEF-2 | FRYER | [10 empty] | 775 | 797
KEF-3 | DISHES | [10 empty] | 525 | 537
EF-1 | [13 empty] | 75 | 77
EF-2 | [13 empty] | 150 | 116
TOTALS |  | 7500 | 7408 | 3850 | 3891 | 3650 | 3517 |  |  | 0 | 0 | 3000 | 2937 | 225 | 193
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3650 | 3517 |  | FRONT |  | 0.005 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3225 | 3130 |  | SIDE |  | 0.007 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 425 | 387 |  | REAR |  | 0.0006 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0042 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0