## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3500 | 3493 | 2750 | 2746 | 750 | 747 | 21.43% | 21.39%
RTU-2 | DINING | 3500 | 3501 | 2750 | 2730 | 750 | 771 | 21.43% | 22.02%
MUA-1 | KITCHEN HD | [8 empty] | 1300 | 1303
EF-1 | KITCHEN HD | [10 empty] | 2550 | 2508
EF-2 | RESTROOM | [12 empty] | 150 | 151
TOTALS |  | 7000 | 6994 | 5500 | 5476 | 1500 | 1518 |  |  | 1300 | 1303 | 2550 | 2508 | 150 | 151
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2800 | 2821 |  | FRONT |  | -0.0008 | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 2700 | 2659 |  | SIDE |  | -0.0014 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 100 | 162 |  | REAR |  | -0.0017 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | -0.0013 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
Building is negative (-0.0024", -0.0027", -0.0029") with all HVAC equipment off. Net average change with equipment on is 0.0013"
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0