## Sheet1
APPENDIX *RTU (ROOFTOP UNIT) *EH (ENTRY HEATER) *ERV (ENERGY RECOVERY VENTILATOR) *EF (EXHAUST FAN) *CU (SPLIT SYSTEM- COMPRESOR UNIT) *AHU(SPLIT SYSTEM-AIR HANDLER) |  |  | 5058 WALGREENS FY24 HVAC SITE SURVEY CHECKLIST
Date: 5/1/25 |  | Store#:5058 |  | Address: 776 Jeffco Blvd. Arnold MO 63010
| EQUIPMENT DATA | [7 empty] | COOLING | HEATING |  | SMOKE DETECTOR |  | POWER SUPPLY |  |  |  | RTU/ROOF |  |  | CURB MEASUREMENTS
RTU DATA | Area Served (LOCATION) EX: Front Sales Pharmacy Storage PARTNER SPACE etc | DATE OF MFG. | EF (ROOF MOUNTED/IN-LINE) | MAKE | MODEL # | SERIAL # | INTERNAL & EXTERNAL UNIT CONDITION COMMENTS & NOTES: (*Give Full Details On Each Unit*) |  | CAPACITY TONS | HEAT TYPE PROPANE / NATURAL GAS / ELECTRIC / HEAT PUMP - AUX HEAT KW | HEATING CAPACITY MAX INPUT(BTU / KW) | LOCATION (UNIT / DUCT) | DUCT LOCATION (SUPPLY / RETURN) | GFI POWERED (Y/N) (BLDG. / RTU) | VOLTAGE (NAMEPLATE) | VOLTAGE (MEASURED) | PHASE | IF NEAREST EDGE OF RTU IS <10' FROM THE EDGE OF THE ROOF PROVIDE DISTANCE BETWEEN THE TWO EDGES (in) | DOES ROOF HAVE A PARAPET? (Y/N) | DOES RTU/HVAC EQUIPMENT UTALIZE OSHA ROOFTOP GUARD RAILS? (Y/N) | EXISTING CURB ADAPTER (YES/NO) | CURB MEASUREMENTS O.D. | UNIT MEASUREMENTS O.D.
RTU 1 | Sales | 2016 | FY25 Age & Condition | York | ZJ120N24R2B5GAA1A1 | N1M6184616 | Carrier New Production 10 Ton Reheat RTU, No DCV, Gas heat, Economizer Curb Adapter Required. Condenser coil has Hail Damage Has a homemade inspection cover for return.Unit is using return air temp sensor for temp control. |  | 10 ton | Gas | 240000 |  |  | Building | 208 | 209 | 3 |  | yes |  | yes
RTU 2 | Sales / Manger Office | 1999 | FY25 ERF Received | Trane | YFD121C3HAAA | P27101346D | Carrier New Production 7.5 Ton RTU, DCV, Gas heat, Economizer Curb Adapter Required. Condenser coil has hail damage. Has homemade cover for burner access panel. |  | 10 Ton | Gas | 250000 |  |  | Building | 208 | 210 | 3 |  | Yes |  | No | 104 X 68 | 107 X 71
RTU 3 | Middle Sales | 1999 | FY25 Age & Condition | Trane | YCD91D3HCBE | P27100924D | Carrier New Production 6 Ton RTU, DCV, Gas heat, Economizer Curb Adapter Required. Condenser Coil has hali damage. Has homemade cover for filter door door. Top cover has some damage by econmizer. |  | 7.5 Ton | Gas | 205000 |  |  | Building | 208 | 209 | 3 |  | Yes |  | No | 82.5 X 47.5 | 87.5 X 50
RTU 4 | Health And Beauty Sales | 1999 | FY25 Age & Condition | Trane | YCD091D3HCBE | P27100876D | York / AES FY24 WV Inventory ZT090N12R2B5GCL2R2 / N2K3906789, Reheat, No DCV, Economizer, Curb Adapter Required. Coil has hail damage. Door hindges broken on filter door. |  | 7.5 | Gas | 205000 |  |  | Building | 208 | 209 | 3 |  | Yes |  | No | 82.5 X 47.5 | 87.5 X 50
RTU 5 | Pharmacy | 1999 | FY25 Age & Condition | Trane | YCD061C3LABF | P27100847D | York / AES FY24 WV Inventory ZJ061N08D2B5GCA2R4 / N2M3986397, DCV, Economizer, Curb Adapter Required. CostGard drain has been broken off and just regular drain attached. Condenser fan motor very loud. |  | 5 Ton | Gas | 90000 |  |  | Building | 208 | 210 | 3 |  | Yes |  | No | 82.5 X 47.5 | 87.5 X 50
RTU 6 | Stock | 1999 | FY25 Age & Condition | Trane | YFD049C3LABF | P2710008323D | York / AES FY24 WV Inventory ZJ049N12D2B5GCA1R3 / N2K3862116, DCV, Economizer, Curb Adapter Required. CostGard drain has been broken off and just regular drain attached. |  | 4 Ton | Gas | 90000 |  |  | Building | 208 | 210 | 3 |  | Yes |  | No | 78.5 X 43.5 | 83.5 X 47
RTU 7
EH | Entrance Heater | 2016 | FY25 Age & Condition | Sterling | RT25 | M1601481351001001 | York / Sterling New Production PV-200 Entranc Heater, 200,000 Gas Input, 115/1/60 power, Curb Adapter TBD by York / AES. Something is not wired correctly. Looks to only have single phase line voltage. Checked voltage between l1 & l2 was only 121 Volts. |  | N/A | Gas | 250000 |  |  | NO | 115 | 121 | 1 |  | Yes |  | No | 98 X 41 | 103.5 X 42
SPLIT SYSTEM DATA
CU 1 | [6 empty] | *include line set sizes*
CU 2 | [6 empty] | *include line set sizes*
CU 3 | [6 empty] | *include line set sizes*
AHU 1
AHU 2
AHU 3
EVAPORATIVE COOLER/SWAMP COOLER
VENTILATION DATA
ERV 1
ERV 2
STOCK ROOM SF
STOCK ROOM EF
EF 1 | Men's Restroom | 1999 | Ceiling |  |  |  | Reuse if Operating |  |  | ELE |  |  |  |  | 115 | 122 | 1
EF 2 | Women's Restroom | 1999 | Ceiling |  |  |  | Reuse if Operating |  |  | ELE |  |  |  |  | 115 | 121 | 1
EF 3 | Breakroom | 1999 | Ceiling |  |  |  | Reuse if Operating |  |  | ELE |  |  |  |  | 115 | 122 | 1
EF 4 | Managers Office | 1999 | Ceiling |  |  |  | Reuse if Operating |  |  | ELE |  |  |  |  | 115 | 121 | 1
EF 5 | Photo Lab | 1999 | Ceiling |  |  |  | Remove and Cap at Ceiling and duct to Roof.
EF 6
EF 7
General Store Notes | [6 empty] | Electrical Panel Information | FUSED SWITCH OR BREAKER | FUSE / BREAKER BRAND | FUSE / BREAKER MODEL # | RATING(AMPS) | WIRE SIZE | CONDUIT SIZE AT UNIT
Former Rite Aid (Y/N): | [6 empty] | RTU-1 | BREAKER | GE | THQB32070 | 70 | 4 | 1
Partner Tenant (included but not lmited to: ex. Village Medical (VMD), LabCorp, Novant, and MedExpress) |  |  | Provid partner name |  |  |  | RTU-2 | BREAKER | GE | THQB32070 | 70 | 4 | 1
If Partner Tenant Exists do they have full height walls? (Y/N) |  |  | Full height walls are defined as walls up to ceiling. |  |  |  | RTU-3 | BREAKER | GE | THQB32060 | 60 | 6 | 0.75
Obvious "non-typical" Heat Load (Y/N) provide detail in note section | NO |  | Ex.: Floor to glass windows, Sky Lights, Permanent Heat Productin Displays, Etc (please make high level note of any potential items.) |  |  |  | RTU-4 | BREAKER | GE | THQB32060 | 60 | 6 | 0.75
Tenant Space (Y/N): | NO |  | Tenant Name (VMD/Kroger/LabCorp, etc.): |  |  |  | RTU-5 | BREAKER | GE | THQB32040 | 40 | 8 | 0.75
Photo Lab (Y/N): | Yes |  | Dry/Wet Lab: |  |  |  | RTU-6 | BREAKER | GE | THQB32030 | 30 | 10 | 0.75
Roof Condition (Good/Fair/Poor): | FAIR | [5 empty] | RTU-7
Ductwork Type (Galvanized, Duct Board, Sock Duct, Other) | Galvanized |  | If "Other" Specify Type: |  |  |  | RTU-8
Unit Hail Damage (Y/N): | Yes | [5 empty] | CU 1
Store within 20 Miles of Ocean? (Y/N): | NO | [5 empty] | CU 2
Existing EMS (Y/N): | Yes |  | EMS Type(FSG/Gridpoint): Gridpoint EC-2000 |  |  |  | CU 3
Fire Alarm Panel Operational (Y/N): | Yes |  | Panel Model#: |  |  |  | AHU 1
Photo of Fire Alarm Panel Taken (Y/N): | Yes | [5 empty] | AHU 2
Main Refrigeration Type (Remote Condensing Unit or Self-Contained) | Remote | [5 empty] | AHU 3
Main Refridgeration Type (Walk-In or Reach-In) | Freezer: Reach-In | [5 empty] | EVAPORATIVE COOLER/SWAMP COOLER
| Cooler: Reach-In | [5 empty] | STOCK ROOM SF
Self-Contained Refrigeration ONLY Door Count: | Freezer: | [5 empty] | STOCK ROOM EF
Cooler:
Obvious Visual Damage to MDP (Y/N): |  |  | Explain Visual Damage:
Notes for Installer: | Recommendation: Replace (5) 1999 Trane, (1) 2016 York RTUs and (1) 2016 Sterling Entry heater per ERF Received and based on Age / Condition. Replace with (3) New Production Carrier RTUs and (3) FY24 AES WV Inventory York RTUs. (1) New Production Sterling Entrance Heater. IC to install Interior humidity Sensors for RTUs (1) and (4) at existing Zone Temperature Sensor Locations. Connect Replacement Equipment to existing GridPoint EC-2000 System as Thermostat control. Remove Photo Ceiling Exhaust Fan and cap at Ceiling and Duct to roof. Reuse remaining roof Exhaust Fans if operating. Entrance Heater name plate has ratings at 3ph 208 volts but unit only has 1ph 110 volts ran to it. It is on a 30amp single pole breaker.
Original Curb Dimensional Data
RTU# | RTU1 | RTU2 | RTU3 | RTU4 | RTU5 | RTU6 | RTU7 | EH
Curb Type | 3 | 3 | 3 | 3 | 3 | 3
A (Length) | 104 | 104 | 82.5 | 82.5 | 82.5 | 78.5
B (Width) | 68 | 68 | 47.5 | 47.5 | 47.5 | 43.5
E Supply | 28.5 | 28.5 | 16.5 | 16.5 | 16.5 | 13 |  | 35 X 19
F Return | 21 | 21 | 13.5 | 13.5 | 13.5 | 12 |  | 35 X 19
G | 21 | 21 | 23 | 23 | 23 | 23
H
I
J
K
L
M
N
O