## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3500 | 3515 | 3000 | 2976 | 500 | 539 | 14.29% | 15.33%
RTU-2 | DINING | 3000 | 3018 | 2000 | 2017 | 1000 | 1001 | 33.33% | 33.17%
MUA-1 | KITCHEN HOOD | [8 empty] | 1950 | 1964
EF-1 | KITCHEN HOOD | [10 empty] | 1600 | 1620
EF-2 | KITCHEN HOOD | [10 empty] | 1600 | 1620
EF-3 | RESTROOM | [12 empty] | 150 | 155
TOTALS |  | 6500 | 6533 | 5000 | 4993 | 1500 | 1540 |  |  | 1950 | 1964 | 3200 | 3240 | 150 | 155
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3450 | 3504 |  | FRONT |  | 0.004" | [8 empty] | FALSE | TRUE | FALSE
TOTAL EXHAUST |  | 3350 | 3395 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 100 | 109 |  | REAR |  | -0.04 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | -0.04 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
[1] HIGH WINDS ON BACK DOOR CAUSING HIGH NEGATIVE READING. UNABLE TO MEASURE ACCURATE BUILDING PRESSURE.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 10 16X16 |  |  |  | ACPSP |  | 183X12 |  | 1950 |  | 3200 |  | -1250