## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8000 | 7427 | 6200 | 5661 | 1800 | 1766 | 22.5% | 23.78%
AC-2 | SIDE DINING/ RR | 2830 | 2749 | 2080 | 2039 | 750 | 710 | 26.5% | 25.83%
AC-3 | DRIVE THUR/ SIDE DINING | 4000 | 4131 | 3000 | 3113 | 1000 | 1018 | 25% | 24.64%
AC-4 | SIDE DINING | 2765 | 2901 | 2165 | 2315 | 600 | 586 | 21.7% | 20.2%
AC-5 | PLAY AREA | 1800 | 1698 | 1500 | 1404 | 300 | 294 | 16.67% | 17.31%
AC-6 | BOH | 1080 | 1134 | 955 | 1016 | 125 | 118 | 11.57% | 10.41%
EF-1 | HD 1 | [10 empty] | 1700 | 1693
EF-2 | HD 2 | [10 empty] | 700 | 683
EF-3 | RESTROOMS | [12 empty] | 400 | 416
EF4 | HD 3 | [10 empty] | 701 | 742
EF 5 | HD L1
TOTALS |  | 20475 | 20040 | 15900 | 15548 | 4575 | 4492 |  |  | 0 | 0 | 3101 | 3118 | 400 | 416
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4575 | 4492 |  | FRONT |  | 0.011 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3501 | 3534 |  | SIDE |  | 0.0107 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1074 | 958 |  | REAR |  | 0.0087 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.010133 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390