## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 3000 | 2946 | 1950 | 1897 | 1050 | 1049 | 35% | 35.61%
RTU-2 | KITCHEN | 3800 | 3833 | 1500 | 1543 | 2300 | 2290 | 60.53% | 59.74%
FC-1 | OFFICE |  |  |  |  | 50 | 46 | #DIV/0! | #DIV/0!
EF-1 | GRILL 1 | [10 empty] | 700 | 715
EF-2 | GRILL 2 | [10 empty] | 700 | 707
EF-3 | FRYER 1 | [10 empty] | 700 | 736
EF-4 | FRYER 2 | [10 empty] | 700 | 715
EF-1 | RESTROOMS | [12 empty] | 300 | 293
EF-2 | UTILITY | [12 empty] | 200 | 214
TOTALS |  | 6800 | 6779 | 3450 | 3440 | 3400 | 3385 |  |  | 0 | 0 | 2800 | 2873 | 500 | 507
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3400 | 3385 |  | FRONT |  | 0.0036 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3300 | 3380 |  | SIDE |  | 0.0049 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 5 |  | REAR |  | -0.0028 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0019 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 2350 | 2336
TOTAL KITCHEN EXHAUST |  | 2800 | 2873
NET AIRFLOW |  | -450 | -537
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0