## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 8750 | 8786 | 7000 | 7164 | 1750 | 1622 | 20% | 18.46%
AC-2 | DRIVE THRU | 5250 | 4962 | 4350 | 4047 | 900 | 915 | 17.14% | 18.44%
AC-3 | SERVING/DINNING | 5250 | 5201 | 3650 | 3696 | 1600 | 1505 | 30.48% | 28.94%
AC-4 | MULTI-PURPOSE | 1875 | 1857 | 1375 | 1365 | 500 | 492 | 26.67% | 26.49%
AC-5 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
AC-6 |  |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | HOOD 1 | [10 empty] | 1913 | 1949
EF-2 | HOOD 2 & 3 | [10 empty] | 1402 | 1349
EF-3 | RESTROOM | [12 empty] | 375 | 380
EF-3 | HOOD 1
TOTALS |  | 21125 | 20806 | 16375 | 16272 | 4750 | 4534 |  |  | 0 | 0 | 3315 | 3298 | 375 | 380
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4750 | 4534 |  | FRONT |  | 0.0123 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3690 | 3678 |  | SIDE |  | 0.011 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1060 | 856 |  | REAR |  | 0.013 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0121 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390