## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6150 | 6035 | 4400 | 4276 | 1750 | 1759 | 28.46% | 29.15%
RTU-2 | KITCHEN | 6150 | 6125 | 4400 | 4224 | 1750 | 1901 | 28.46% | 31.04%
PRV2 | HOOD 1 | [10 empty] | 1500 | 1530
PRV3 | HOOD 2 | [10 empty] | 1500 | 1553
PRV-1 | RESTROOM | [12 empty] | 375 | 369
EF-1A | MOP ROOM | [12 empty] | 75 | 74
TOTALS |  | 12300 | 12160 | 8800 | 8500 | 3500 | 3660 |  |  | 0 | 0 | 3000 | 3083 | 450 | 443
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3500 | 3660 |  | FRONT |  | 0.0051 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3450 | 3526 |  | SIDE |  | 0.0041 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | 134 |  | REAR |  | 0.0012 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0034667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0