## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6150 | 5766 | 4400 | 4054 | 1750 | 1712 | 28.46% | 29.69%
RTU-2 | KITCHEN | 6150 | 5581 | 4400 | 3728 | 1750 | 1853 | 28.46% | 33.2%
PRV2 | HOOD 1 | [10 empty] | 1500 | 1530
PRV3 | HOOD 2 | [10 empty] | 1500 | 1553
PRV-1 | RESTROOM | [12 empty] | 375 | 369
EF-1A | MOP ROOM | [12 empty] | 75 | 0
TOTALS |  | 12300 | 11347 | 8800 | 7782 | 3500 | 3565 |  |  | 0 | 0 | 3000 | 3083 | 450 | 369
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3500 | 3565 |  | FRONT |  | 0.0086 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3450 | 3452 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | 113 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0086 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
OA couldn't be read due to high windy conditions. OA was found by subtracting the exhaust readings from supply, and was confirmed using building pressure.
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0