## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 4000 | 3933 | 2850 | 2837 | 1150 | 1096 | 28.75% | 27.87%
RTU-2 | KITCHEN | 5000 | 4883 | 4650 | 4540 | 350 | 343 | 7% | 7.024%
FCU-1 | MGRS OFFICE |  |  |  |  | 40 | 42 | #DIV/0! | #DIV/0!
MUA-1 | COOKLINE | [8 empty] | 3300 | 3239
KEF-1 | HOOD 2 | [10 empty] | 1967 | 2053
KEF-2 | HOOD 1 | [10 empty] | 1967 | 2009
EF-1 | RESTROOMS | [12 empty] | 300 | 308
TOTALS |  | 9000 | 8816 | 7500 | 7377 | 1540 | 1481 |  |  | 3300 | 3239 | 3934 | 4062 | 300 | 308
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4840 | 4720 |  | FRONT |  | 0.0146 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4234 | 4370 |  | SIDE |  | 0.0137 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 606 | 350 |  | REAR |  | 0.0125 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0136 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
KITCHEN PRESSURIZATION (MUST BE NEGATIVE)
TOTALS |  | DESIGN | ACTUAL
TOTAL KITCHEN OA |  | 3690 | 3624
TOTAL KITCHEN EXHAUST |  | 3934 | 4062
NET AIRFLOW |  | -244 | -438
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0