## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
DOAS-1 | DINING | 5850 | 5881 | 4100 | 4060 | 1750 | 1821 | 29.91% | 30.96%
DOAS-2 | KITCHEN | 6150 | 6184 | 4450 | 4407 | 1700 | 1777 | 27.64% | 28.74%
PRV-2 | HOOD1 | [10 empty] | 1500 | 1536
PRV-3 | HOOD2 | [10 empty] | 1500 | 1522
PRV-1 | RESTROOM | [12 empty] | 375 | 371
EF-1A | MOP ROOM | [12 empty] | 75 | 70
TOTALS |  | 12000 | 12065 | 8550 | 8467 | 3450 | 3598 |  |  | 0 | 0 | 3000 | 3058 | 450 | 441
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3450 | 3598 |  | FRONT |  | 0.0047 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3450 | 3499 |  | SIDE |  | 0.0079 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 99 |  | REAR |  | 0.0031 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0052333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0