## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6150 | 6264 | 4250 | 4290 | 1900 | 1974 | 30.89% | 46%
RTU-2 | \KITCHEN | 6150 | 5963 | 4250 | 4107 | 1900 | 1856 | 30.89% | 48%
PRV-2 | HOOD 1 | [10 empty] | 1500 | 1559
PRV-3 | HOOD 2 | [10 empty] | 1500 | 1652
PRV-4/EF1A | HOOD 3 | [10 empty] | 350 | 317
PRV-1 | RESTROOM | [12 empty] | 300 | 282
EF-1 | MOP ROOM | [12 empty] | 75 | 73
TOTALS |  | 12300 | 12227 | 8500 | 8397 | 3800 | 3830 |  |  | 0 | 0 | 3350 | 3528 | 375 | 355
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | FALSE | FALSE | TRUE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 3800 | 3830 |  | FRONT |  | 0.014 | [8 empty] | FALSE | FALSE | TRUE
TOTAL EXHAUST |  | 3725 | 3883 |  | SIDE |  | -0.001 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 0
NET AIRFLOW |  | 75 | -53 |  | REAR |  | 0.014 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.009 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0