## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | SIDE DINING | 3400 | 3616 | 2450 | 2727 | 950 | 889 | 27.94% | 24.59%
AC-2 | KITCHEN | 8000 | 7683 | 6200 | 5715 | 1800 | 1968 | 22.5% | 25.61%
AC-3 | DINING | 4920 | 4760 | 3700 | 3475 | 1220 | 1285 | 24.8% | 27%
AC-4 | PLAYGROUND | 2000 | 2085 | 1650 | 1704 | 350 | 381 | 17.5% | 18.27%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1941
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1091 | 1017
EF-3 | RESTROOM | [12 empty] | 350 | 343
TOTALS |  | 18320 | 18144 | 14000 | 13621 | 4320 | 4523 |  |  | 0 | 0 | 3003 | 2958 | 350 | 343
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4320 | 4523 |  | FRONT |  | 0.032 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3353 | 3301 |  | SIDE |  | 0.027 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 967 | 1222 |  | REAR |  | 0.034 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.031 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390