## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | BOH | 2250 | 2184 | 1975 | 1900 | 275 | 284 | 12.22% | 13%
RTU-2 | STOCKROOM | 2250 | 2236 | 1925 | 1912 | 325 | 324 | 14.44% | 14.49%
RTU-3 | STOCKROOM | 4800 | 4587 | 3465 | 2655 | 1335 | 1932 | 27.81% | 42.12%
RTU-4 | SALES | 4000 | 3754 | 2885 | 3492 | 1115 | 262 | 27.88% | 6.979%
RTU-5 | SALES | 3800 | 3740 | 3800 | 3740 | 0 | 0 | 0% | 0%
RTU-6 | SALES |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
RTU-7 | FRONT SALES |  |  | 0 | 0 |  |  | #DIV/0! | #DIV/0!
EF-1 | RESTROOMS | [12 empty] | 325 | 320
TOTALS |  | 17100 | 16501 | 14050 | 13699 | 3050 | 2802 |  |  | 0 | 0 | 0 | 0 | 325 | 320
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3050 | 2802 |  | FRONT |  | 0.0472 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 325 | 320 |  | SIDE |  | 0.065 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 2725 | 2482 |  | REAR |  | 0.0486 | [8 empty] | FALSE
[5 empty] | AVERAGE |  | 0.0536 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0