## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HOOD ON OA |  | HOOD OFF OA |  | HOOD ON EXHAUST |  | HOOD OFF EXHAUST
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | SALES | 865 | 894 | 415 | 426
RTU-2 | SALES | 865 | 894 | 415 | 413
RTU-3 | KITCHEN | 865 | 894 | 415 | 413
RTU-4 | BOH | 160 | 161 | 160 | 161
EF-1 | MEN'S RR/COMBI |  |  |  |  | 650 | 719 | 650 | 719
EF-2 | WOMEN'S RR |  |  |  |  | 350 | 335 | 350 | 335
EF-3 | HOOD |  |  |  |  | 1350 | 1410 | 0 | 0
TOTALS |  | 2755 | 2843 | 1405 | 1413 | 2350 | 2464 | 1000 | 1054
HOOD ON
[10 empty] | TRUE | FALSE | FALSE
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL | [6 empty] | TRUE | FALSE | FALSE
TOTAL OA |  | 2755 | 2843 |  |  | FRONT |  | 0.005
TOTAL EXHAUST |  | 2350 | 2464 |  |  | SIDE |  | 0.005 |  | TRUE
NET AIRFLOW |  | 405 | 379 |  |  | REAR |  | 0.005
[6 empty] | AVERAGE |  | 0.005
HOOD OFF
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 1405 | 1413 |  |  | FRONT
TOTAL EXHAUST |  | 1000 | 1054 |  |  | SIDE
NET AIRFLOW |  | 405 | 359 |  |  | REAR
AVERAGE
NOTES:
Could not measure BP w/ hood off due to kitchen equip. being in use. Shouldn't be any issues per balance schedule.