## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HOOD ON OA |  | HOOD OFF OA |  | HOOD ON EXHAUST |  | HOOD OFF EXHAUST
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU 1 | SALES | 800 | 851 | 350 | 360
RTU-2 | SALES | 800 | 853 | 350 | 364
RTU-3 | BOH/KITCHEN | 800 | 853 | 350 | 362
EF-1 | RR/JANITOR |  |  |  |  | 750 | 809 | 750 | 809
EF-3 | HOOD |  |  |  |  | 1350 | 1371 | 0 | 0
TOTALS |  | 2400 | 2557 | 1050 | 1086 | 2100 | 2180 | 750 | 809
HOOD ON
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 2400 | 2557 |  |  | FRONT |  | 0.003 |  | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2100 | 2180 |  |  | SIDE |  | 0.003
NET AIRFLOW |  | 300 | 377 |  |  | REAR |  | 0 |  | TRUE
[6 empty] | AVERAGE |  | 0.002
HOOD OFF
NET AIRFLOW CALCULATION | [5 empty] | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20)
TOTALS |  | DESIGN | ACTUAL
TOTAL OA |  | 1050 | 1086 |  |  | FRONT
TOTAL EXHAUST |  | 750 | 809 |  |  | SIDE
NET AIRFLOW |  | 300 | 277 |  |  | REAR
AVERAGE
NOTES:
Due to Kitchen already being in use, could not turn hood off for 'Hood OFF' building pressure. Based on balance sheet, there shouldn't be any building issues w/ hood off.