## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 8696 | 8050 | 7269 | 1450 | 1427 | 15.26% | 16.41%
AC-2 | SERVING, DT | 5600 | 5401 | 4025 | 3874 | 1575 | 1527 | 28.12% | 28.27%
AC-3 | DINING | 6400 | 6205 | 4375 | 4169 | 2025 | 2036 | 31.64% | 32.81%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1955
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1494
EF-3 | RESTROOM | [12 empty] | 695 | 705
TOTALS |  | 21500 | 20302 | 16450 | 15312 | 5050 | 4990 |  |  | 0 | 0 | 3314 | 3449 | 695 | 705
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 5050 | 4990 |  | FRONT |  | 0.0069 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 4009 | 4154 |  | SIDE |  | 0.0059 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1041 | 836 |  | REAR |  | 0.0074 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0067333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390