## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 6150 | 6163 | 4250 | 4310 | 1900 | 1853 | 30.89% | 30.07%
RTU-2 | KITCHEN | 6750 | 6397 | 4850 | 4554 | 1900 | 1843 | 28.15% | 28.81%
PRV-2 | HOOD1 | [10 empty] | 1500 | 1505
PRV-3 | HOOD2 | [10 empty] | 1500 | 1422
PRV-4 | HOOD3 | [10 empty] | 350 | 338
PRV 1 | RESTROOM | [12 empty] | 375 | 361
EFA 1 | MOP ROOM | [12 empty] | 75 | 69
TOTALS |  | 12900 | 12560 | 9100 | 8864 | 3800 | 3696 |  |  | 0 | 0 | 3350 | 3265 | 450 | 430
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3800 | 3696 |  | FRONT |  | -0.0001 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3800 | 3695 |  | SIDE |  | 0.0005 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 0 | 1 |  | REAR |  | 0.0001 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00016667 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0