## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AC-1 | KITCHEN | 9500 | 9307 | 8450 | 8235 | 1050 | 1072 | 11.05% | 11.52%
AC-2 | SERVING | 5250 | 5266 | 3675 | 3690 | 1575 | 1576 | 30% | 29.93%
AC-3 | DINING | 6000 | 6380 | 3975 | 4324 | 2025 | 2056 | 33.75% | 32.23%
EF-1 | HD1 L+R PRESS COOKER | [10 empty] | 1912 | 1961
EF-2 | HD2/HD3 FRYERS | [10 empty] | 1402 | 1460
EF-3 | RESTROOM | [12 empty] | 300 | 306
TOTALS |  | 20750 | 20953 | 16100 | 16249 | 4650 | 4704 |  |  | 0 | 0 | 3314 | 3421 | 300 | 306
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 4650 | 4704 |  | FRONT |  | 0.0088 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3614 | 3727 |  | SIDE |  | 0.0032 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 1036 | 977 |  | REAR |  | 0.0025 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0048333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 1080 |  | -1080
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 832 |  | -832
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 701 |  | -701
HD | HALTON | [5 empty] | NA |  | NA |  | 0 |  | 390 |  | -390