## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | DINING | 2700 | 2499 | 2100 | 1850 | 600 | 649 | 22.22% | 25.97%
RTU-2 | COUNTER | 2700 | 2560 | 2100 | 1909 | 600 | 651 | 22.22% | 25.43%
RTU-3 | KITCHEN | 3500 | 3427 | 2700 | 2565 | 800 | 862 | 22.86% | 25.15%
MAU-1 | FRYER HOOD | [8 empty] | 0 | 0
EF1 | HOO | [10 empty] | 1900 | 1900
EF-2 | RR | [12 empty] | 64 | 64
EF-3 | RR | [12 empty] | 60 | 60
TOTALS |  | 8900 | 8486 | 6900 | 6324 | 2000 | 2162 |  |  | 0 | 0 | 1900 | 1900 | 64 | 64
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2000 | 2162 |  | FRONT |  | 0.007 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 1964 | 1964 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 36 | 198 |  | REAR |  | 0.0095 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.00825 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0