## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3430 | 2650 | 2642 | 750 | 788 | 22.06% | 22.97%
RTU-2 | DINING ROOM | 4000 | 3951 | 3250 | 3236 | 750 | 715 | 18.75% | 18.1%
MUA-1 | HOOD MUA | [8 empty] | 1950 | 1932
EF-1 | HOOD FAN | [10 empty] | 3200 | 3224
EF-2 | RESTROOM | [12 empty] | 150 | 152
TOTALS |  | 7400 | 7381 | 5900 | 5878 | 1500 | 1503 |  |  | 1950 | 1932 | 3200 | 3224 | 150 | 152
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 3450 | 3435 |  | FRONT |  | 0.0005 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 3350 | 3376 |  | SIDE |  | 0.0003 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 100 | 59 |  | REAR |  | 0.014 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0049333 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0