## AHU2
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: AHU2 |  | Area: EXPANSION
Unit Data |  |  | Test Data
Manufacurer | TRANE |  |  | Design | Actual
Model Number | CSAA050UA |  | SF CFM | 22000
Serial Number |  |  | SF RPM | 1852
Configuration | HORIZONTAL |  | RA CFM | 20700
No. Pre Filters / Size | 1 / 16X20X4 |  | OA CFM | 1300
No. Pre Filters / Size | 4 / 16X25X4 |  | RL VOLTAGE | 460
No. Pre Filters / Size | 12 / 20X25X4 |  | RL AMPERAGE | 24.5
|  |  | Motor B.H.P. | 30.258
Motor Data |  |  | Performance Data
Motor MFG |  |  |  | Design | Actual
Frame |  |  | Suction S.P.
HP | 20 |  | Discharge S.P.
RPM | 1800 |  | Total SP | 5.57
Phase | 3 |  | CW Coil P.D. | 0.877
Volts | 460 |  | HW Coil P.D. | 0.060
Amps | 24.5 |  | Final Filters P.D.
Heat Wheel P.D.
|  |  | Pre Filters P.D. | 1.70
|  |  | Total ESP | 2.7

## AHU2 VAV's
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: AHU2 Single Duct VAV's
Asset | Area Served |  | Type | Size | Design Max CFM | Actual Max CFM | Design Min CFM | Actual Min CFM | Design Heat CFM | Actual Heat CFM | Ak (max)
AHU2-0-1 | A-001 |  | HEAT | 8 | 300 |  | 0 |  | 300
AHU2-1-1 | A-102 | NOTE | HEAT | 10 | 325 |  | 0 |  | 325
AHU2-1-2 | A-102 |  | HEAT | 10 | 975 |  | 230 |  | 650
AHU2-1-3 | A-129 |  | HEAT | 8 | 675 |  | 175 |  | 355
AHU2-1-4 | A-128 |  | HEAT | 10 | 1010 |  | 320 |  | 610
AHU2-1-5 | A-131 |  | HEAT | 8 | 500 |  | 145 |  | 145
AHU2-1-6 | A-106 |  | HEAT | 10 | 600 |  | 230 |  | 450
AHU2-1-7 | A-109 |  | HEAT | 8 | 450 |  | 145 |  | 425
AHU2-1-8 | A-140 |  | HEAT | 8 | 250 |  | 250 |  | 250
AHU2-1-9 | A-124 |  | HEAT | 10 | 880 |  | 230 |  | 250
AHU2-1-10 | A-139 |  | HEAT | 8 | 500 |  | 175 |  | 175
AHU2-1-11 | A-136 |  | HEAT | 8 | 550 |  | 225 |  | 225
AHU2-1-12 | A-113 |  | HEAT | 8 | 450 |  | 145 |  | 225
AHU2-1-13 | A-120 |  | HEAT | 10 | 660 |  | 230 |  | 460
AHU2-1-14 | A-115 |  | HEAT | 10 | 650 |  | 230 |  | 540
AHU2-1-15 | A-117 |  | HEAT | 10 | 750 |  | 230 |  | 675
AHU2-1-16 | A-118 |  | HEAT | 8 | 550 |  | 185 |  | 400
AHU2-1-17 |  | NOTE
AHU2-2-1 |  | NOTE
AHU2-2-2 | A-200 |  | HEAT | 8 | 530 |  | 145 |  | 205
AHU2-2-3 | A-231 |  | HEAT | 10 | 780 |  | 180 |  | 420
AHU2-2-4 | A-230 |  | HEAT | 8 | 560 |  | 145 |  | 265
AHU2-2-5 | A-228 |  | HEAT | 10 | 1050 |  | 290 |  | 440
AHU2-2-6 | A-244 |  | HEAT | 8 | 450 |  | 170 |  | 170
AHU2-2-7 | A-203 |  | HEAT | 8 | 260 |  | 145 |  | 145
AHU2-2-8 | A-207 |  | HEAT | 10 | 700 |  | 145 |  | 420
AHU2-2-9 | A-209 |  | HEAT | 8 | 345 |  | 145 |  | 225
AHU2-2-10 | A-210 |  | HEAT | 6 | 150 |  | 85 |  | 110
AHU2-2-11 | A-242 |  | HEAT | 6 | 250 |  | 250 |  | 250
AHU2-2-12 | A-240 |  | HEAT | 6 | 200 |  | 100 |  | 100
AHU2-2-13 | A-223 |  | HEAT | 10 | 900 |  | 250 |  | 440
AHU2-2-14 | A-221 |  | HEAT | 10 | 825 |  | 230 |  | 230
AHU2-2-15 | A-238 |  | HEAT | 8 | 550 |  | 225 |  | 225
AHU2-2-16 | A-213 |  | HEAT | 10 | 700 |  | 230 |  | 500
AHU2-2-17 | A-216 |  | HEAT | 8 | 370 |  | 145 |  | 270
AHU2-2-18 | A-218 |  | HEAT | 10 | 675 |  | 230 |  | 590
AHU2-2-19 | A-219 |  | HEAT | 8 | 575 |  | 170 |  | 320
AHU2-2-NEW | A-201 | NOTE | HEAT |  | 1590 |  | 330 |  | 850
NOTES: | AHU2-0-1 DUCT WITHOUT DIFFUSER SERVING SHELL SPACE A-001 IN BASEMENT.
AHU2-1-1 Diffuser total is 650 CFM, VAV design max is 325 CFM per schedule and submittal
AHU2-1-17 Listed in submittal, deleted on bulletin 17 AIR drawing along with riser from FLR1 to FLR 2. Shows on Hydro drawing (bulletin 17).
AHU2-2-1 Listed in schedule, not shown in submittal or on any drawing
AHU2-2-NEW Unnamed new VAV serving A-201, TSTAT in unnamed room. Basic stats from drawing (not on submittal)
Note on C7: NTAB: BILLINGSLEY ONLY

## FLR 1 VAV SGRD's (1)
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: FLR 1 VAV SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-1-1 | A-102 | LD4 | 10 | 650 |  |  | 0
AHU2-1-1 |  |  |  | 650 |  | 0 | 0
1-2-1 | A-102 | LD3 | 8 | 175 |  |  | 0
1-2-2 | A-101 | LD1 | 6 | 110 |  |  | 0
1-2-3 | A-101 | LD1 | 6 | 120 |  |  | 0
1-2-4 | A-101 | LD1 | 6 | 110 |  |  | 0
1-2-5 | A-101 | LD1 | 6 | 120 |  |  | 0
1-2-6 | A-101 | LD1 | 6 | 110 |  |  | 0
1-2-7 | A-101 | LD1 | 6 | 120 |  |  | 0
1-2-8 | A-101 | LD1 | 6 | 110 |  |  | 0
AHU2-1-2 |  |  |  | 975 |  | 0 | 0
1-3-1 | A-102 | LD3 | 8 | 150 |  |  | 0
1-3-2 | A-129 | LD2 | 10 | 175 |  |  | 0
1-3-3 | A-129 | LD2 | 10 | 175 |  |  | 0
1-3-4 | A-129 | LD2 | 10 | 175 |  |  | 0
AHU2-1-3 |  |  |  | 675 |  | 0 | 0
1-4-1 | A-128 | LD2 | 8 | 150 |  |  | 0
1-4-2 | A-128 | LD2 | 8 | 150 |  |  | 0
1-4-3 | A-128 | LD2 | 8 | 150 |  |  | 0
1-4-4 | A-127 | LD2 | 8 | 140 |  |  | 0
1-4-5 | A-127 | LD2 | 8 | 140 |  |  | 0
1-4-6 | A-126 | LD2 | 8 | 140 |  |  | 0
1-4-7 | A-126 | LD2 | 8 | 140 |  |  | 0
AHU2-1-4 |  |  |  | 1010 |  | 0 | 0
1-5-1 | A-130 | D1 | 8 | 150 |  |  | 0
1-5-2 | A-131 | D1 | 10 | 250 |  |  | 0
1-5-3 | A-141 | D1 | 8 | 100 |  |  | 0
AHU2-1-5 |  |  |  | 500 |  | 0 | 0
1-6-1 | A-108 | LD1 | 8 | 150 |  |  | 0
1-6-2 | A-107 | LD1 | 8 | 150 |  |  | 0
1-6-3 | A-106 | LD1 | 8 | 150 |  |  | 0
1-6-4 | A-105 | LD1 | 8 | 150 |  |  | 0
AHU2-1-6 |  |  |  | 600 |  | 0 | 0

## FLR 1 VAV SGRD's (2)
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: FLR 1 VAV SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-7-1 | A-109 | LD2 | 8 | 125 |  |  | 0
1-7-2 | A-109 | LD2 | 8 | 125 |  |  | 0
1-7-3 | A-109 | LD2 | 8 | 125 |  |  | 0
1-7-4 | A-109 | LD2 | 6 | 75 |  |  | 0
AHU2-1-7 |  |  |  | 450 |  | 0 | 0
1-8-1 | A-140 | D1 | 8 | 125 |  |  | 0
1-8-2 | A-133 | D1 | 8 | 125 |  |  | 0
AHU2-1-8 |  |  |  | 250 |  | 0 | 0
1-9-1 | A-125 | LD1 | 12 | 220 |  |  | 0
1-9-2 | A-124 | LD1 | 12 | 220 |  |  | 0
1-9-3 | A-123 | LD1 | 12 | 220 |  |  | 0
1-9-4 | A-122 | LD1 | 12 | 220 |  |  | 0
AHU2-1-9 |  |  |  | 880 |  | 0 | 0
1-10-1 | A-138 | D1 | 8 | 100 |  |  | 0
1-10-2 | HALL | LD2 | 8 | 150 |  |  | 0
1-10-3 | A-139 | D1 | 8 | 100 |  |  | 0
1-10-4 | HALL | LD2 | 8 | 150 |  |  | 0
AHU2-1-10 |  |  |  | 500 |  | 0 | 0
1-11-1 | A-135 | D1 | 8 | 150 |  |  | 0
1-11-2 | A-136 | D1 | 8 | 150 |  |  | 0
1-11-3 | HALL | LD2 | 8 | 150 |  |  | 0
1-11-4 | A-137 | D1 | 6 | 100 |  |  | 0
AHU2-1-11 |  |  |  | 550 |  | 0 | 0
1-12-1 | A-111 | LD1 | 8 | 150 |  |  | 0
1-12-2 | A-112 | LD1 | 8 | 150 |  |  | 0
1-12-3 | A-113 | LD1 | 8 | 150 |  |  | 0
AHU2-1-12 |  |  |  | 450 |  | 0 | 0
1-13-1 | A-121 | LD1 | 12 | 220 |  |  | 0
1-13-2 | A-120 | LD1 | 12 | 220 |  |  | 0
1-13-3 | A-119 | LD1 | 12 | 220 |  |  | 0
AHU2-1-13 |  |  |  | 660 |  | 0 | 0

## FLR 1 VAV SGRD's (3)
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: FLR 1 VAV SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
1-14-1 | A-114 | LD1 | 8 | 150 |  |  | 0
1-14-2 | A-115 | LD1 | 8 | 125 |  |  | 0
1-14-3 | A-115 | LD1 | 8 | 125 |  |  | 0
1-14-4 | A-116 | LD1 | 8 | 125 |  |  | 0
1-14-5 | A-116 | LD1 | 8 | 125 |  |  | 0
AHU2-1-14 |  |  |  | 650 |  | 0 | 0
1-15-1 | A-117 | LD2 | 8 | 175 |  |  | 0
1-15-2 | A-117 | LD2 | 8 | 135 |  |  | 0
1-15-3 | A-117 | LD2 | 8 | 135 |  |  | 0
1-15-4 | A-117 | LD2 | 8 | 175 |  |  | 0
1-15-5 | A-117 | LD2 | 8 | 130 |  |  | 0
AHU2-1-15 |  |  |  | 750 |  | 0 | 0
1-16-1 | A-118 | LD2 | 8 | 150 |  |  | 0
1-16-2 | A-118 | LD2 | 6 | 100 |  |  | 0
1-16-3 | A-118 | LD2 | 8 | 150 |  |  | 0
1-16-4 | A-118 | LD2 | 8 | 150 |  |  | 0
AHU2-1-16 |  |  |  | 550 |  | 0 | 0

## FLR 2 VAV SGRD's (1)
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: FLR 2 VAV SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2-2-1 | A-200 | LD1 | 8 | 165 |  |  | 0
2-2-2 | A-202 | LD5 | 48 | 200 |  |  | 0
2-2-3 | A-200 | LD1 | 8 | 165 |  |  | 0
AHU2-2-2 |  |  |  | 530 |  | 0 | 0
2-3-1 | A-231 | LD1 | 8 | 150 |  |  | 0
2-3-2 | A-231 | LD1 | 8 | 150 |  |  | 0
2-3-3 | A-231 | LD1 | 8 | 140 |  |  | 0
2-3-4 | A-231 | LD1 | 8 | 140 |  |  | 0
2-3-5 | A-202 | LD5 | 48 | 200 |  |  | 0
AHU2-2-3 |  |  |  | 780 |  | 0 | 0
2-4-1 | A-230 | LD2 | 8 | 120 |  |  | 0
2-4-2 | A-230 | LD2 | 8 | 120 |  |  | 0
2-4-3 | A-230 | LD2 | 8 | 120 |  |  | 0
AHU2-2-4 |  |  |  | 360 |  | 0 | 0
2-5-1 | A-229 | LD1 | 12 | 225 |  |  | 0
2-5-2 | A-228 | LD1 | 12 | 225 |  |  | 0
2-5-3 | HALL | LD1 | 8 | 150 |  |  | 0
2-5-4 | A227 | LD1 | 12 | 225 |  |  | 0
2-5-5 | A-226 | LD1 | 12 | 225 |  |  | 0
AHU2-2-5 |  |  |  | 1050 |  | 0 | 0
2-6-1 | A-232 | D1 | 8 | 100 |  |  | 0
2-6-2 | HALL | LD1 | 8 | 150 |  |  | 0
2-6-3 | A-244 | D1 | 8 | 100 |  |  | 0
2-6-4 | A-243 | D1 | 8 | 100 |  |  | 0
AHU2-2-6 |  |  |  | 450 |  | 0 | 0
2-7-1 | A-203 | LD3 | 48 | 130 |  |  | 0
2-7-2 | A-203 | LD3 | 48 | 130 |  |  | 0
AHU2-2-7 |  |  |  | 260 |  | 0 | 0
2-8-1 | A-208 | LD1 | 10 | 175 |  |  | 0
2-8-2 | A-207 | LD1 | 10 | 175 |  |  | 0
2-8-3 | A-206 | LD1 | 10 | 175 |  |  | 0
2-8-4 | A-205 | LD1 | 10 | 175 |  |  | 0
AHU2-2-8 |  |  |  | 700 |  | 0 | 0

## FLR 2 VAV SGRD's (2)
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: FLR 2 VAV SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2-9-1 | A-209 | LD2 | 6 | 110 |  |  | 0
2-9-2 | A-209 | LD2 | 6 | 110 |  |  | 0
2-9-3 | A-209 | LD2 | 8 | 125 |  |  | 0
AHU2-2-9 |  |  |  | 345 |  | 0 | 0
2-10-1 | A-210 | LD1 | 8 | 150 |  |  | 0
AHU2-2-10 |  |  |  | 150 |  | 0 | 0
2-11-1 | A-242 | D1 | 8 | 125 |  |  | 0
2-11-2 | A-235 | D1 | 8 | 125 |  |  | 0
AHU2-2-11 |  |  |  | 250 |  | 0 | 0
2-12-1 | A-241 | D1 | 8 | 100 |  |  | 0
2-12-2 | A-240 | D1 | 8 | 100 |  |  | 0
AHU2-2-12 |  |  |  | 200 |  | 0 | 0
2-13-1 | A-225 | LD1 | 12 | 225 |  |  | 0
2-13-2 | A-224 | LD1 | 12 | 225 |  |  | 0
2-13-3 | A-223 | LD1 | 12 | 225 |  |  | 0
2-13-4 | A-222 | LD1 | 12 | 225 |  |  | 0
AHU2-2-13 |  |  |  | 900 |  | 0 | 0
2-14-1 | A-221 | LD2 | 12 | 225 |  |  | 0
2-14-2 | HALL | LD1 | 8 | 150 |  |  | 0
2-14-3 | A-221 | LD2 | 12 | 225 |  |  | 0
2-14-4 | A-220 | LD2 | 12 | 225 |  |  | 0
AHU2-2-14 |  |  |  | 825 |  | 0 | 0
2-15-1 | A-237 | D1 | 8 | 150 |  |  | 0
2-15-2 | A-238 | D1 | 8 | 150 |  |  | 0
2-15-3 | HALL | LD1 | 8 | 150 |  |  | 0
2-15-4 | A-239 | D1 | 8 | 100 |  |  | 0
AHU2-2-15 |  |  |  | 550 |  | 0 | 0

## FLR 2 VAV SGRD's (3)
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: FLR 2 VAV SGRD's
Asset | Area Served | Type | Size | DESIGN CFM | Prelim CFM | FINAL CFM | % to design
2-16-1 | A-212 | LD1 | 8 | 150 |  |  | 0
2-16-2 | A-213 | LD1 | 8 | 150 |  |  | 0
2-16-3 | A-214 | LD2 | 8 | 150 |  |  | 0
2-16-4 | A-215 | LD2 | 8 | 125 |  |  | 0
2-16-5 | A-215 | LD2 | 8 | 125 |  |  | 0
AHU2-2-16 |  |  |  | 700 |  | 0 | 0
2-17-1 | A-216 | LD2 | 8 | 115 |  |  | 0
2-17-2 | A-216 | LD2 | 8 | 115 |  |  | 0
2-17-3 | A-217 | LD2 | 8 | 140 |  |  | 0
AHU2-2-17 |  |  |  | 370 |  | 0 | 0
2-18-1 | A-218 | LD2 | 8 | 135 |  |  | 0
2-18-2 | A-218 | LD2 | 8 | 135 |  |  | 0
2-18-3 | A-218 | LD2 | 8 | 135 |  |  | 0
2-18-4 | A-218 | LD2 | 8 | 135 |  |  | 0
2-18-5 | A-218 | LD2 | 8 | 135 |  |  | 0
AHU2-2-18 |  |  |  | 675 |  | 0 | 0
2-19-1 | A-219 | LD2 | 8 | 125 |  |  | 0
2-19-2 | A-219 | LD2 | 8 | 125 |  |  | 0
2-19-3 | A-219 | LD2 | 8 | 75 |  |  | 0
2-19-4 | A-219 | LD2 | 8 | 125 |  |  | 0
2-19-5 | A-219 | LD2 | 8 | 125 |  |  | 0
AHU2-2-19 |  |  |  | 575 |  | 0 | 0
2-NEW-1 |  | LD | 6 | 175 |  |  | 0
2-NEW-2 |  | LD | 6 | 250 |  |  | 0
2-NEW-3 | A-201 | LD1 | 6 | 105 |  |  | 0
2-NEW-4 | A-201 | LD1 | 6 | 120 |  |  | 0
2-NEW-5 | A-201 | LD1 | 6 | 105 |  |  | 0
2-NEW-6 | A-201 | LD1 | 6 | 105 |  |  | 0
2-NEW-7 | A-201 | LD1 | 6 | 120 |  |  | 0
2-NEW-8 | A-201 | LD1 | 6 | 105 |  |  | 0
2-NEW-9 | A-201 | LD1 | 6 | 120 |  |  | 0
2-NEW-10 | A-202 | LD4 | 72 | 390 |  |  | 0
AHU2-1-NEW |  |  |  | 1595 |  | 0 | 0

## RF2
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: RF2 |  | Area: AHU2 RETURN
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | QMXD-HP |  | CFM | 22000
Serial Num |  |  | Fan RPM | 813
Type | MIXED FLOW |  | RL Voltage | 480
RL Amperage
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 1.5
Frame
Horsepower | 15
Motor Rpm | 860
Phase | 3
Voltage (rated) | 480
Amperage (rated)
Service Factor
-

## EF7
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: EF7 |  |  | Area: RR EXHAUST
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | ACE-D VF |  |  | CFM | 1300
Serial Num |  |  |  |  | Fan RPM | 1712
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 7.4
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1
Frame
Horsepower |  | 0.75
Motor Rpm |  | 1725
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
E7-1 | A-236 | R1 | 22X10 | 75 |  |  | 0
E7-2 | A-235 | R1 | 22X10 | 225 |  |  | 0
E7-3 | A-242 | R1 | 22X10 | 225 |  |  | 0
E7-4 | A-134 | R1 | 22X10 | 75 |  |  | 0
E7-5 | A-133 | R1 | 22X10 | 225 |  |  | 0
E7-6 | A-140 | R1 | 22X10 | 225 |  |  | 0
NOTE | A-001 | DUCT |  |  |  |  | #DIV/0!
|  |  |  | 1050 |  | 0 | 0
NOTES: | DUCT WITHOUT GRILLE SERVING SHELL SPACE A-001 IN BASEMENT.
-

## EF8
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: EF8 |  |  | Area: ELEC RM EXHAUST
Unit Data |  |  |  |  | Test Data
MFG |  | COOK |  |  |  | Design | Actual
Model Num |  | ACE-D VF |  |  | CFM | 700
Serial Num |  |  |  |  | Fan RPM | 2006
Type |  | CRE DNBLAST |  |  | RL Voltage | 115
[5 empty] | RL Amperage | 4.4
Motor Data |  |  |  |  | Suction ESP
Motor MFG |  |  |  |  | Total ESP | 1
Frame
Horsepower |  | 0.33
Motor Rpm |  | 2800
Phase |  | 1
Voltage (rated) |  | 115
Amperage (rated)
Service Factor
Asset | Area Served | Type | Size | DESIGN | CFM(1) | FINAL CFM | % to design
8-1 | A-234 | R2 | 10X10 | 100 |  |  | 0
8-2 | A-003 | R2 | 18X10 | 600 |  |  | 0
|  |  |  | 700 |  | 0 | 0
-

## EF9
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: EF9 |  | Area: MECH RM EXHAUST (005)
Unit Data |  |  | Test Data
MFG | COOK |  |  | Design | Actual
Model Num | SQN-D VF |  | CFM | 500
Serial Num |  |  | Fan RPM | 1501
Type | INLINE |  | RL Voltage | 115
|  |  | RL Amperage | 2.4
Motor Data |  |  | Suction ESP
Motor MFG |  |  | Total ESP | 0.5
Frame
Horsepower | 0.167
Motor Rpm | 1725
Phase | 1
Voltage (rated) | 15
Amperage (rated)
Service Factor
-

## Boiler
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: BOILER |  | Service: HOT WATER
Unit Data | B2
Manufacturer | RBI
Model Number | MB3000
Serial Number
Test Data | Design | Actual
Water Flow GPM | 175
Water Press. Drop

## Chiller AC
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: CH2
UNIT DATA
Unit Description | AIR-COOLED SCROLL
Manufacturer | TRANE
Model Number | CGAM070F2
Serial Number
EVAPORATOR DATA | Design | Actual
Flow GPM | 139.9
Pressure Drop | 16.1

## HWP1
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: HWP1 |  | Service: HOT WATER
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-1510 2.5AC |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in) | 5.375
Service | HW DISTRIBUTION |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head | 330 / 75 |  | Discharge Pressure (ft)
Impellar Diameter | 5.375 |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 75
Motor Data |  |  | Final GPM
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 460
Horsepower | 10 |  | RL Amperage
Motor RPM | 3600 |  | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## HWP2
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: HWP2 |  | Service: HOT WATER
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-1510 2.5AC |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in) | 5.375
Service | HW DISTRIBUTION |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head | 330 / 75 |  | Discharge Pressure (ft)
Impellar Diameter | 5.375 |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 75
Motor Data |  |  | Final GPM
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 460
Horsepower | 10 |  | RL Amperage
Motor RPM | 3600 |  | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## BP2
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: BP2 |  | Service: HOT WATER
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-80 4X4X11B |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in) | 10
Service | BOILER PUMP |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head | 175 / 40 |  | Discharge Pressure (ft)
Impellar Diameter | 10 |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 40
Motor Data |  |  | Final GPM
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 460
Horsepower | 5 |  | RL Amperage
Motor RPM | 1150 |  | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## HCP1
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: HCP1 |  | Service: HOT WATER
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-90 1.25AAB |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in) | 7.75
Service | HW COIL CIRCULATION |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head | 45 / 20 |  | Discharge Pressure (ft)
Impellar Diameter | 5.0 |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 20
Motor Data |  |  | Final GPM
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 120
Horsepower | 0.50 |  | RL Amperage
Motor RPM | 1800 |  | BHP
Phase | 1
Voltage | 120
Amperage
Service Factor
Efficiency
Power Factor

## CHWP1
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: CHWP1 |  | Service: CHILLED WATER
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-80SC 5X5X7B |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in) | 6.5
Service | CH1 PUMP |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head | 360 / 35 |  | Discharge Pressure (ft)
Impellar Diameter | 6.5 |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 35
Motor Data |  |  | Final GPM
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 460
Horsepower | 7.5 |  | RL Amperage
Motor RPM | 1800 |  | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## CHWP2
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: CHWP2 |  | Service: CHILLED WATER
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-80SC 3X3X7C |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in) | 6.375
Service | CH2 PUMP |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head | 140 / 35 |  | Discharge Pressure (ft)
Impellar Diameter | 6.375 |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 35
Motor Data |  |  | Final GPM
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 460
Horsepower | 3 |  | RL Amperage
Motor RPM | 1800 |  | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## CHWP3
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: CHWP3 |  | Service: CHILLED WATER
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-80SC 5X5X13.5 |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in) | 10.625
Service | SECONDARY CHW |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head | 500 / 95 |  | Discharge Pressure (ft)
Impellar Diameter | 11.625 |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 95
Motor Data |  |  | Final GPM
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 460
Horsepower | 25 |  | RL Amperage
Motor RPM | 1800 |  | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## CHWP4
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: CHWP4 |  | Service: CHILLED WATER
Unit Data |  |  | Test Data
| Actual |  |  | Design | Actual
MFG | BELL & GOSSETT |  | Pump Off Pressure (psi)
Model Num | e-80SC 5X5X13.5 |  | Pump Dead Head (ft)
Serial Num |  |  | Act. Impellar Dia (in) | 10.625
Service | SECONDARY CHW |  | Valve Open GPM
Pump RPM |  |  | Valve Open Diff (ft)
GPM/Head | 500 / 95 |  | Discharge Pressure (ft)
Impellar Diameter | 11.625 |  | Suction Pressure (ft)
|  |  | Total Head Pressure (ft) | 95
Motor Data |  |  | Final GPM
| Actual |  | Motor Frequency (HZ)
Motor MFG |  |  | System Set Point
Frame |  |  | RL Voltage | 460
Horsepower | 25 |  | RL Amperage
Motor RPM | 1800 |  | BHP
Phase | 3
Voltage | 460
Amperage
Service Factor
Efficiency
Power Factor

## HW CS
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: CIRCUIT SETTERS |  |  | Service: HOT WATER
Asset | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design
UH1-1 |  |  |  |  | 1.3
UH1-2 |  |  |  |  | 1.3
UH1-3 |  |  |  |  | 1.3
AHU2-0-1 |  |  |  |  | 0.9
AHU2 COIL |  |  |  |  | 44.02
CUH2 |  |  |  |  | 1.3
AHU2-1-4 |  |  |  |  | 1.8
AHU2-1-3 |  |  |  |  | 1
AHU2-1-2 |  |  |  |  | 1.9
CUH1 |  |  |  |  | 2.5
AHU2-1-9 |  |  |  |  | 0.7
AHU2-1-13 |  |  |  |  | 1.3
AHU2-1-16 |  |  |  |  | 1.2
AHU2-1-1 |  |  |  |  | 0.9
AHU2-1-5 |  |  |  |  | 0.5
AHU2-1-6 |  |  |  |  | 1.3
AHU2-1-7 |  |  |  |  | 1.2
AHU2-1-8 |  |  |  |  | 0.7
AHU2-1-10 |  |  |  |  | 0.5
AHU2-1-12 |  |  |  |  | 0.6
AHU2-1-11 |  |  |  |  | 0.6
AHU2-1-14 |  |  |  |  | 1.5
AHU2-1-15 |  |  |  |  | 1.9
AHU2-1-17 |  |  |  |  | 1.9
AHU2-2-4 |  |  |  |  | 0.8
AHU2-2-7 |  |  |  |  | 0.5
AHU2-2-3 |  |  |  |  | 1.2
AHU2-2-2 |  |  |  |  | 0.6
AHU2-2-6 |  |  |  |  | 0.5
AHU2-2-8 |  |  |  |  | 1.2
AHU-2-2-9 |  |  |  |  | 0.6
AHU2-2-10 |  |  |  |  | 0.5
AHU-2-2-5 |  |  |  |  | 1.3
AHU2-2-13 |  |  |  |  | 1.3
AHU2-2-11 |  |  |  |  | 0.7
AHU2-2-12 |  |  |  |  | 0.5
AHU2-2-15 |  |  |  |  | 0.6
AHU2-2-14 |  |  |  |  | 0.7
AHU-2-2-19 |  |  |  |  | 0.9
AHU2-2-18 |  |  |  |  | 1.7
AHU-2-2-17 |  |  |  |  | 0.8
AHU-2-2-16 |  |  |  |  | 1.4
NOTES: | AHU2-1-17 Listed in submittal, deleted on bulletin 17 AIR drawing. Shows on Hydro drawing (bulletin 17).

## CHW CS
National TAB
Project: Connor Group Office
Address: 10510 Springboro Pike Miamisburg, OH
Asset: CIRCUIT SETTERS |  |  | Service: CHILLED WATER
Asset | MFG | Model | Size | Type | Design GPM | Setting | Delta P | Final GPM | % to Design
AHU2 COIL |  |  |  |  | 140.2