## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 |  | 3000 | 3068 | 2250 | 2342 | 750 | 726 | 25% | 23.66%
RTU-2 |  | 5000 | 4516 | 3750 | 3331 | 1250 | 1185 | 25% | 26.24%
MUA-1 | [10 empty] | 0
EF-1 | [12 empty] | 964
EF-2 | [12 empty] | 1533
EF-3 | [14 empty] | 510
TOTALS |  | 8000 | 7584 | 6000 | 5673 | 2000 | 1911 |  |  | 0 | 0 | 0 | 2497 | 0 | 510
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 0
TOTAL OA |  | 2000 | 1911 |  | FRONT |  | -0.0326
TOTAL EXHAUST |  | 0 | 3007 |  | SIDE |  | -0.0247 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 2000 | -1096 |  | REAR |  | -0.0234
[5 empty] | AVERAGE |  | -0.0269 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 0
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0 | FALSE | FALSE | TRUE
[16 empty] | TRUE | TRUE | TRUE
FALSE