## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
AHU-1 | SERVICE CORRIDOR | 2000 | 1665 | 1860 | 1545 | 140 | 120 | 7% | 7.207%
AHU-2 | 110D | 1600 | 1660 | 1460 | 1528 | 140 | 132 | 8.75% | 7.952%
AHU-3 | WINE LOCKER | 1200 | 1125 | 940 | 875 | 260 | 250 | 21.67% | 22.22%
AHU-4 | 109A | 1600 | 1832 | 1460 | 1700 | 140 | 132 | 8.75% | 7.205%
AHU-5 | 100F | 2000 | 2117 | 1840 | 1969 | 160 | 148 | 8% | 6.991%
MUA | [9 empty] | 7000 | 6433
KEF-1 | [11 empty] | 6000 | 6519
TOTALS |  | 8400 | 8399 | 7560 | 7617 | 840 | 782 |  |  | 7000 | 6433 | 6000 | 6519 | 0 | 0
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 7840 | 7215 |  | FRONT |  | 0.19" | [8 empty] | #DIV/0! | #DIV/0! | FALSE
TOTAL EXHAUST |  | 6000 | 6519 |  | SIDE |  | 0.184" |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | #DIV/0!
NET AIRFLOW |  | 1840 | 696 |  | REAR | [10 empty] | #DIV/0!
[5 empty] | AVERAGE |  | #DIV/0! |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | #DIV/0!
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0