## Report Sheet
STORE #: | 2913 | [22 empty] | Choose Yes or No: | SELECT FROM DROP DOWN LIST
CITY, STATE: | CIRCLEVILLE, OH | [22 empty] | Yes | 2 END PANEL - 171" HOOD LENGTH
HOOD TYPE: | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH | [22 empty] | No | 2 END PANEL - 156" HOOD LENGTH
DATE: | 2023-03-18 | [23 empty] | 1 END PANEL (PLANHCA) - 156" HOOD LENGTH
TECH NAME: | JORDAN BEST | [23 empty] | 1 END PANEL (PLANCHA) - 171" HOOD LENGTH
1 END PANEL (FRYER) - 156" HOOD LENGTH
1 END PANEL (FRYER) - 171" HOOD LENGTH
UNIT TAG |  |  | UNIT | AREA SERVED | INITIAL |  | FINAL |  | PULLEY CHANGE REQUIRED? | MOTOR RPM |  | FAN RPM |  | POWER
MFG | MODEL | S/N |  |  | DESIGN | INITIAL | GOAL | FINAL |  | INITIAL | FINAL | INITIAL | FINAL | HP | RLV (Initial) | RLV (Final) | PH | FLA | RLA(I) | RLA(F) | BHP(I) | BHP(F) | % Change
YORK | ZJ078N12D2B5EAA2A1 | N1H6890156 | RTU-1 | KITCHEN | 500 | 0 | 0 | 0 |  | 1742 | 1742 | 1038 | 1038 | 2 | 211.8 | 211.8 | 3 | 6.6 | 6.54 | 6.54 | 2.3155 | 2.3155 | 0%
YORK | ZJ102N12D2B5EAA2A1 | N1H6890181 | RTU-2 | DINING | 1000 | 0 | 1000 | 1173 |  | 1757 | 1757 | 926.5 | 926.5 | 3 | 211.4 | 211.4 | 3 | 9.5 | 6.32 | 6.32 | 2.2334 | 2.2334 | 0%
CAPTIVE AIRE | A1-D.250-G10 | 2733328 | MUA-1 | HOOD 1 | 1950 | 2257 | 1700 | 1692 | Yes | 1777 | 1779 | 949 | 948.1 | 3 | 211.7 | 212.9 | 3 | 5.95 | 3.41 | 2.55 | 1.2067 | 0.90752 | -24.8%
CAPTIVE AIRE | NCA24HPFA | 2733328 | EF-1 | HOOD 1 | 3200 | 2912 | 2450 | 2631 | No | 1763 | 1772 | 857 | 773 | 2 | 212.5 | 212.6 | 3 | 5.95 | 3.34 | 2.97 | 1.1864 | 1.0555 | -11.04%
| RR FAN RUNNING? | Yes | EF-2 | RESTROOM | 150 | 150 | 150 | 150
NET BUILDING AIRFLOW CALCULATION
[5 empty] | DESIGN | INITIAL | GOAL | FINAL |  | FINAL B.P. | [5 empty] | ∆ Power | ∆ Load (CFM)
|  |  | TOTAL OA |  | 3450 | 2257 | 2700 | 2865 |  | FRONT DOOR |  | -0.046 |  |  | INITIAL | 6.9421 | 2257
|  |  | TOTAL EXHAUST |  | 3350 | 3062 | 2600 | 2781 |  | BACK DOOR |  | -0.062 |  |  | FINAL | 6.5119 | 2865
|  |  | NET AIRFLOW |  | 100 | -805 | 100 | 84 |  | AVERAGE |  | -0.054 |  |  | ∆ | -0.43016 | 608
Issue List
Unit # | Description
RTU-1 | RTU / OA Filters / OA filters are not installed. Recommend installing
RTU-1 | RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU-2 | RTU / OA Filters / OA filters are not installed. Recommend installing
Additional Notes:

## Issue list (hidden)
Select from drop down list
None
EF / Hood Filters / Exhaust filters are dirty causing airflow to be low initially. Airflow could not be reduced. Recommend deep cleaning or replacement.
EF / Not operational / The EF is not operational. Recommend servicing.
MUA / Intake Filter / The intake air filter is dirty and had to temporarily be removed for testing. Recommend cleaning.
MUA / Not operational / MUA is not operational. Recommend servicing.
MUA / PSP / MUA is low and the PSP appears to be clogged. Unable to decrease MUA. Recommend cleaning.
RTU / Belt / Belt is broken and OA could not be tested.
RTU / Belt / Belt is loose and could not be tightened.
RTU / Filters / RTU filters are dirty. Temporarily removed for testing. Recommend replacement.
RTU / Not running / RTU is not running and could not be overriden on. Recommend servicing
RTU / OA Damper / Outside air damper is not functional and OA could not be set.
RTU / OA Filters / The outside air filters are dirty and had to be temporarily removed for testing. Recommend cleaning.
RTU / OA Filters / OA filters are not installed. Recommend installing
RTU / Thermostats / Gridpoint stats are in Fan Auto. Recommend programming for Fan on except if kitchen RTU is balanced for 0 CFM OA.
RTU / Rotation / Fan rotation is backwards. Unable to set OA. Recommend servicing.