## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | CAFÉ SERV. | 3600 | 3649 | 2700 | 2728 | 900 | 921 | 25% | 25.24%
RTU-2 | CAFÉ SERV. | 4200 | 4280 | 3200 | 3234 | 1000 | 1046 | 23.81% | 24.44%
RTU-3 | SALES | 4400 | 4194 | 3300 | 3142 | 1100 | 1052 | 25% | 25.08%
RTU-4 | SALES | 4400 | 4660 | 3300 | 3457 | 1100 | 1203 | 25% | 25.82%
RTU-5 | SALES | 4400 | 4794 | 3300 | 3663 | 1100 | 1131 | 25% | 23.59%
RTU-6 | OFFICE/BRK | 960 | 1004 | 810 | 842 | 150 | 162 | 15.62% | 16.14%
RTU-7 | SITOCK | 2400 | 2546 | 2250 | 2385 | 150 | 161 | 6.25% | 6.324%
RTU-8 | CAFÉ WRK. | 2100 | 2043 | 2000 | 1938 | 100 | 105 | 4.762% | 5.14%
EF-1 | ELEC. RM | [12 empty] | 750 | 712
EF-2 | REST RMS. | [12 empty] | 300 | 315
EF-3 | SERVER | [12 empty] | 500 | 476
EF-4 | CAFÉ | [12 empty] | 500 | 515
TOTALS |  | 26460 | 27170 | 20860 | 21389 | 5600 | 5781 |  |  | 0 | 0 | 0 | 0 | 2050 | 2018
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 5600 | 5781 |  | FRONT |  | 0.0097 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2050 | 2018 |  | SIDE | [5 empty] | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 3550 | 3763 |  | REAR | [10 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0097 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0
HD | [14 empty] | 0