## SUMMARY (2)
AIR BALANCE SCHEDULE
| AREA | HVAC SUPPLY |  | HVAC RETURN |  | HVAC OUTDOOR |  | OA % |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | GENERAL EXH.
UNIT | SERVED | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL | DESIGN | ACTUAL
RTU-1 | KITCHEN | 3400 | 3294 | 2325 | 2233 | 1075 | 1061 | 31.62% | 32.21%
RTU-2 | DINING | 3400 | 3465 | 2325 | 2379 | 1075 | 1086 | 31.62% | 31.34%
EF-1 | KITCHEN HOOD | [10 empty] | 1900 | 1877
EF-2 | RESTROOM | [12 empty] | 200 | 204
TOTALS |  | 6800 | 6759 | 4650 | 4612 | 2150 | 2147 |  |  | 0 | 0 | 1900 | 1877 | 200 | 204
NET BUILDING AIRFLOW CALCULATION |  |  |  |  | DOOR TESTED |  | BUILDING PRESSURE MEASUREMENTS (IN. H20) |  |  |  | FINAL CHECKS |  |  |  |  | TRUE | FALSE | FALSE
TOTALS |  | DESIGN | ACTUAL | [7 empty] | ACTUAL NET AIRFLOW COINCIDES WITH DESIGN: |  |  |  | 1
TOTAL OA |  | 2150 | 2147 |  | FRONT |  | 0.0055 | [8 empty] | TRUE | FALSE | FALSE
TOTAL EXHAUST |  | 2100 | 2081 |  | SIDE |  | 0.005 |  |  |  | MEASURED PRESSURES COINCIDES WITH ACTUAL NET AIRFLOW: |  |  |  | 1
NET AIRFLOW |  | 50 | 66 |  | REAR |  | 0.006 | [8 empty] | TRUE
[5 empty] | AVERAGE |  | 0.0055 |  |  |  | PRESSURE FALLS WITHIN IMC TOLERANCE OF +/-0.02" W.C. |  |  |  | 1
NOTES:
SYSTEM COMPONENTS TO ASSETS SCHEDULED ABOVE
UNIT | MANUFACTURER |  | FILTER TYPE/#/SIZE |  |  |  | MAU TYPE |  | SIZE |  | HOOD MAKE-UP |  | HOOD EXHAUST |  | NET CFM
HD | CAPTIVE-AIRE |  | SOLO 9 16X16 |  |  |  | ACPSP |  | 165X9 |  | 1300 |  | 2550 |  | -1250